## CNW-AD
SMARTEMP PRODUCT SELECTION CALCULATOR
Circular Nozzle [CNW-AD]
Project: | <Project Name>
Inputs | [5 empty] | Detailed Selection | [7 empty] | v 4.2 [03/2025]
Airflow Rate | 200 | [L/s] | [m3/h] |  |  | Supply Temperature and Deflection
| = 720 | [m³/h]
Maximum Total Pressure | 60 | Pa (default 60 Pa) |  |  |  | ΔT (cooling) | -6 | K (-8 K to 0 K recommended)
Diffuser Height | 5 | m |  |  |  | ΔT (heating) | 6 | K (0 K to + 6 K recommended)
use 0 K for isothermal applications
Horizontal Throw Distance | 24 | m |  |  |  | Jet Velocity
Throw to 0.4 m/s terminal velocity (default)
Throw to 0.2 m/s terminal velocity for sensitive applications
e.g. towards projector screens
Related Products | [5 empty] | Include Swirl Element [Type S1] (for reduced throw and velocity)
Smartemp CSW-AD: | wall mounted, high-induction swirl with adjustable throw settings
Smartemp PMW-AD: | wall mounted, high-induction perforated face solution
Smartemp LMW-AD: | wall-mounted, high-induction linear slot solution
Smartemp JSC-AD: | a vertical discharge solution suitable for ultra-high ceilings
| SMARTEMP CNW-AD |  |  | DN200 [S0] | DN250 [S0] | DN315 [S0] | DN400 [S0] | DN500 [S0] | DN630 [S0] | Sizes DN100, DN125, DN160 available on request
Airflow | Selected Airflow Rate |  | [L/s] | 200 | 200 | 200 | 200 | 200 | 200
Pressure * | Static Pressure @ Airflow |  | [Pa] | 279.3 | 106.4 | 39.6 | 12.7 | 4.4 | < 3 | Key: | Suitable | Not Suitable | Warning/Warning
| Total Pressure @ Airflow |  | [Pa] | 304.1 | 116.5 | 43.7 | 14.2 | 5.1 | < 3
| Max Selected Pressure |  | [Pa] | 60 | 60 | 60 | 60 | 60 | 60
Acoustics * | Sound Power Level |  | [dB(A)] | 51.5 | 34.1 | 16.4 | < 4 | < 4 | < 4
Throw & Velocity | Isothermal Throw Distance |  | [m] | 38.7 | 31 | 24 | 18.1 | 14.2 | 11.1
| Jet Velocity at 24m |  | [m/s] | 0.63 | 0.51 | 0.39 | 0.3 | 0.23 | 0.18
Jet Temperature | Jet ΔT at 24 m (cooling) |  | [K] | -0.1 | -0.1 | -0.1 | -0.2 | -0.2 | -0.3
| Jet ΔT at floor level (heating) |  | [K] | 0.1 | 0.2 | 0.3 | 0.5 | 0.8 | 1.3
Discharge & Installation Angle | Recommended Discharge Angle (cool) |  | [°] | -5 | 1 | 16 | 44 | 66 | 78
| Recommended Discharge Angle (heat) |  | [°] | -15 | -18 | -24 | -33 | -43 | -62
| Total Arc of Rotation (θ) |  | [°] | 9 | 20 | 40 | 76 | 109 | 140 | Note: θ < 60° (Manual & Electric motor) ; θ < 40° (Thermal Element )
| Recommended Mounting Angle (φ) |  | [°] | 0 | 0 | 0 | -3 | -13 | -32 | * Pressure and Sound Power Level valid for manual diffuser
| Min Centreline Distance ** |  | [m] | 0.32 | 0.41 | 0.52 | 0.69 | 0.89 | 1.13 | ** Refer to 'Notes' worksheet for example
Product Code
| Select Size |  |  | DN200 | DN250 | DN315 | DN400 | DN500 | DN630 | Sizes DN100, DN125, DN160 available on request
| Swirl Element |  |  |  |  | No swirl element | (see cell F17)
| Adjustment Type |  |  | Manual |  | Electric Motor |  | Thermal Element |  | Manual & Electric Motor θ < 60° ; Thermal Element θ < 40° (Row 34)
| Face Colour (Powder Coated) |  |  | RAL9003* |  | RAL9005 |  | custom |  | RAL9003 - Signal White
| Order Code (select to copy) |  |  | please select a valid size in row 41 | [5 empty] | go to 'CNW-AD Selection Summary' for a printable summary of the selection
* note: not to scale
[5 empty] | click to see product on smartair.asia | [7 empty] | Copyright © 2021 SMARTAIR DIFFUSION
Group Box 19
Group Box 34
Group Box 37
Group Box 44
Group Box 48

## CNW-ADequations (hidden)
Units
Unit Selection | 1 | [L/s] | L/s
Unit Multiplier | 1
Airflow Rate | 200
Airflow convert | 720 | alternate | [m³/h]
Input Values
Airflow Rate | 200 | [6 empty] | 630 | 377 | 142129 | 163.3%
Pressure | 60 | [6 empty] | 500 | 295 | 87025 | 163.1%
Height | 5 | [6 empty] | 400 | 231 | 53361 | 174.2%
Distance | 24 | 24 m | [5 empty] | 315 | 175 | 30625 | 168%
Swirl | FALSE | 0 | [5 empty] | 250 | 135 | 18225 | 156.2%
[8 empty] | 200 | 108 | 11664
terminal velocity selection | 1 |  | 1 | 0.4
terminal velocity | 0.4 | m/s | 2 | 0.2
dT cool | -6
dt heat | 6
Heating to hit above floor level | 1.5 | m
Input Diagonal Distance | 24.5153
Jet Decay Constant 'k' | 10.48
Centreline distance mulptiplier | 3 | x exit diameter | [21 empty] | Deflection constant x 2 for swirl
200 | Type 0 |  |  | 250 | Type 0 |  |  | 315 | Type 0 |  |  | 400 | Type 0 |  |  | 500 | Type 0 |  |  | 630 | Type 0 |  |  | 250 | Type 1 |  |  | 315 | Type 1 |  |  | 400 | Type 1 |  |  | 500 | Type 1 |  | 630 | Type 1 |  | 160 | TEST
Diameter | 108 |  |  | Diameter | 135 |  |  | Diameter | 174 |  |  | Diameter | 231 |  |  | Diameter | 295 |  |  | Diameter | 377 | mm |  | Diameter | 135 |  |  | Diameter | 174 |  |  | Diameter | 231 |  |  | Diameter | 295 |  | Diameter | 377 |  | Diameter | 86.4
Diameter | 0.108 | m |  | Diameter | 0.135 | m |  | Diameter | 0.174 | m |  | Diameter | 0.231 | m |  | Diameter | 0.295 | m |  | Diameter | 0.377 | m |  | Diameter | 0.135 | m |  | Diameter | 0.174 | m |  | Diameter | 0.23 | m |  | Diameter | 0.295 |  | Diameter | 0.377 | m | Diameter | 0.0864 | m
Area | 0.0091609 |  |  | Area | 0.014314 |  |  | Area | 0.023779 |  |  | Area | 0.04191 |  |  | Area | 0.068349 |  |  | Area | 0.11163 |  |  | Area | 0.014314 |  |  | Area | 0.023779 |  |  | Area | 0.041548 |  |  | Area | 0.068349 |  | Area | 0.11163 |  | Area | 0.005863
Velocity | 21.832 |  |  | Velocity | 13.9725 |  |  | Velocity | 8.4109 |  |  | Velocity | 4.7722 |  |  | Velocity | 2.9261 |  |  | Velocity | 1.7917 |  |  | Velocity | 13.9725 |  |  | Velocity | 8.4109 |  |  | Velocity | 4.8138 |  |  | Velocity | 2.9261 |  | Velocity | 1.7917 |  | Velocity | 0
data.TotalPressure | 50 |  |  | data.TotalPressure | 50 |  |  | data.TotalPressure | 50 |  |  | data.TotalPressure | 50 |  |  | data.TotalPressure | 50 |  |  | data.TotalPressure | 50
data.Flowrate | 81.1 |  |  | data.Flowrate | 131 |  |  | data.Flowrate | 214 |  |  | data.Flowrate | 375 |  |  | data.Flowrate | 628 |  |  | data.Flowrate | 893
Total Pressure Loss (Pa) | 304.0803 |  |  | Total Pressure Loss (Pa) | 116.5433 |  |  | Total Pressure Loss (Pa) | 43.6719 |  |  | Total Pressure Loss (Pa) | 14.2222 |  |  | Total Pressure Loss (Pa) | 5.0712 |  |  | Total Pressure Loss (Pa) | 2.508 |  |  | Total Pressure Loss (Pa) | 179.8264 |  |  | Total Pressure Loss (Pa) | 67.3858 |  |  | Total Pressure Loss (Pa) | 21.9449 |  |  | Total Pressure Loss (Pa) | 7.8249 |  | Total Pressure Loss (Pa) | 3.8698 |  | Total Pressure Loss (Pa) | 0
Duct Area | 0.031416 |  |  | Duct Area | 0.049087 |  |  | Duct Area | 0.077931 |  |  | Duct Area | 0.12566 |  |  | Duct Area | 0.19635 |  |  | Duct Area | 0.31172 |  |  | Duct Area | 0.049087 |  |  | Duct Area | 0.077931 |  |  | Duct Area | 0.12566 |  |  | Duct Area | 0.19635 |  | Duct Area | 0.31172
Duct Velocity | 6.3662 |  |  | Duct Velocity | 4.0744 |  |  | Duct Velocity | 2.5664 |  |  | Duct Velocity | 1.5915 |  |  | Duct Velocity | 1.0186 |  |  | Duct Velocity | 0.64159 |  |  | Duct Velocity | 4.0744 |  |  | Duct Velocity | 2.5664 |  |  | Duct Velocity | 1.5915 |  |  | Duct Velocity | 1.0186 |  | Duct Velocity | 0.64159
Duct Dyn Pressure | 24.8237 |  |  | Duct Dyn Pressure | 10.1678 |  |  | Duct Dyn Pressure | 4.0341 |  |  | Duct Dyn Pressure | 1.5515 |  |  | Duct Dyn Pressure | 0.63549 |  |  | Duct Dyn Pressure | 0.25213 |  |  | Duct Dyn Pressure | 10.1678 |  |  | Duct Dyn Pressure | 4.0341 |  |  | Duct Dyn Pressure | 1.5515 |  |  | Duct Dyn Pressure | 0.63549 |  | Duct Dyn Pressure | 0.25213 |  | Duct Dyn Pressure | 0
Duct Static Pressure | 279.2566 |  |  | Duct Static Pressure | 106.3755 |  |  | Duct Static Pressure | 39.6379 |  |  | Duct Static Pressure | 12.6707 |  |  | Duct Static Pressure | 4.4357 |  |  | Duct Static Pressure | 2.2559 |  |  | Duct Static Pressure | 169.6586 |  |  | Duct Static Pressure | 63.3517 |  |  | Duct Static Pressure | 20.3934 |  |  | Duct Static Pressure | 7.1894 |  | Duct Static Pressure | 3.6177 |  | Duct Static Pressure | 0
Direct Throw Distance | 38.7122 |  |  | Direct Throw Distance | 30.9697 |  |  | Direct Throw Distance | 24.0282 |  |  | Direct Throw Distance | 18.0992 |  |  | Direct Throw Distance | 14.1726 |  |  | Direct Throw Distance | 11.09 |  |  | Direct Throw Distance | 16.7404 |  |  | Direct Throw Distance | 12.9882 |  |  | Direct Throw Distance | 9.8259 |  |  | Direct Throw Distance | 7.6609 |  | Direct Throw Distance | 5.9946 |  | Direct Throw Distance | 0
(Isothermal Direct) Throw (m) | 38.7122 | 38.3879 |  | (Isothermal Direct) Throw (m) | 30.9697 | 30.5635 |  | (Isothermal Direct) Throw (m) | 24.0282 | 23.5023 |  | (Isothermal Direct) Throw (m) | 18.0992 | 17.3949 |  | (Isothermal Direct) Throw (m) | 14.1726 | 13.2613 |  | (Isothermal Direct) Throw (m) | 11.09 | 9.8988 |  | (Isothermal Direct) Throw (m) | 16.7404 | 15.9763 |  | (Isothermal Direct) Throw (m) | 12.9882 | 11.9873 |  | (Isothermal Direct) Throw (m) | 9.8259 | 8.4586 |  | (Isothermal Direct) Throw (m) | 7.6609 | 5.8042 | (Isothermal Direct) Throw (m) | 5.9946 | 3.3068 | (Isothermal Direct) Throw (m) | 0 | 0
Jet Velocity at Distance | 0.63164 |  |  | Jet Velocity at Distance | 0.50531 |  |  | Jet Velocity at Distance | 0.39205 |  |  | Jet Velocity at Distance | 0.29531 |  |  | Jet Velocity at Distance | 0.23124 |  |  | Jet Velocity at Distance | 0.18095 |  |  | Jet Velocity at Distance | 0.25808 |  |  | Jet Velocity at Distance | 0.20024 |  |  | Jet Velocity at Distance | 0.15148 |  |  | Jet Velocity at Distance | 0.1181 |  | Jet Velocity at Distance | 0.092416 |  | Jet Velocity at Distance | 0
SWL A | 20.2 |  |  | SWL A | 20.2 |  |  | SWL A | 20.2 |  |  | SWL A | 20.2 |  |  | SWL A | 20.2 |  |  | SWL A | 20.2 |  |  | SWL A | 14.2 |  |  | SWL A | 14.2 |  |  | SWL A | 14.2 |  |  | SWL A | 14.2 |  | SWL A | 14.2
SWL B | -64 |  |  | SWL B | -62 |  |  | SWL B | -59.9 |  |  | SWL B | -57 |  |  | SWL B | -54.8 |  |  | SWL B | -52.7 |  |  | SWL B | -13.4 |  |  | SWL B | -13.4 |  |  | SWL B | -13.4 |  |  | SWL B | -13.4 |  | SWL B | -13.4
SWL (dB(A)) | 51.4893 |  |  | SWL (dB(A)) | 34.1169 |  |  | SWL (dB(A)) | 16.3895 |  |  | SWL (dB(A)) | -3.3729 |  |  | SWL (dB(A)) | -22.0037 |  |  | SWL (dB(A)) | -34.1264 |  |  | SWL (dB(A)) | 61.9124 | + 5 dbA buffer |  | SWL (dB(A)) | 50.1786 | + 5 dbA buffer |  | SWL (dB(A)) | 36.7088 | + 5 dbA buffer |  | SWL (dB(A)) | 24.1896 | + 5 dbA buffer | SWL (dB(A)) | 16.3219 | + 5 dbA buffer | SWL (dB(A)) | #NUM! | + 5 dbA buffer
Cooling Angle |  |  |  | Cooling Angle |  |  |  | Cooling Angle |  |  |  | Cooling Angle |  |  |  | Cooling Angle |  |  |  | Cooling Angle |  |  |  | Cooling Angle |  |  |  | Cooling Angle |  |  |  | Cooling Angle |  |  |  | Cooling Angle |  |  | Cooling Angle |  |  | Cooling Angle
dT at Distance (cool) | -0.088108 |  |  | dT at Distance (cool) | -0.11014 |  |  | dT at Distance (cool) | -0.14195 |  |  | dT at Distance (cool) | -0.18845 |  |  | dT at Distance (cool) | -0.24067 |  |  | dT at Distance (cool) | -0.30756 |  |  | dT at Distance (cool) | -0.055068 |  |  | dT at Distance (cool) | -0.070976 |  |  | dT at Distance (cool) | -0.093819 |  |  | dT at Distance (cool) | -0.12033 |  | dT at Distance (cool) | -0.15378 |  | dT at Distance | -0.036
deflection constant k | -0.00019341 |  |  | deflection constant k | -0.00037776 |  |  | deflection constant k | -0.00080884 |  |  | deflection constant k | -0.0018926 |  |  | deflection constant k | -0.0039417 |  |  | deflection constant k | -0.008227 |  |  | deflection constant k | -0.00075552 |  |  | deflection constant k | -0.0016177 |  |  | deflection constant k | -0.0037362 |  |  | deflection constant k | -0.0078834 |  | deflection constant k | -0.016454
Deflection (cool) | -2.8497 |  |  | Deflection (cool) | -5.5658 |  |  | Deflection (cool) | -11.9173 |  |  | Deflection (cool) | -27.8846 |  |  | Deflection (cool) | -58.0758 |  |  | Deflection (cool) | -121.214 |  |  | Deflection (cool) | -11.1317 |  |  | Deflection (cool) | -23.8345 |  |  | Deflection (cool) | -55.0481 |  |  | Deflection (cool) | -116.1515 |  | Deflection (cool) | -242.4281 |  | Deflection (cool) | #DIV/0!
Discharge Angle | -5.1198 |  |  | Discharge Angle | 1.3506 |  |  | Discharge Angle | 16.078 |  |  | Discharge Angle | 43.6372 |  |  | Discharge Angle | 65.6683 |  |  | Discharge Angle | 78.3316 |  |  | Discharge Angle | 14.3317 |  |  | Discharge Angle | 38.1238 |  |  | Discharge Angle | 64.3805 |  |  | Discharge Angle | 77.8157 |  | Discharge Angle | 84.228 |  | Discharge Angle | #DIV/0!
Heating Angle |  |  |  | Heating Angle |  |  |  | Heating Angle |  |  |  | Heating Angle |  |  |  | Heating Angle |  |  |  | Heating Angle |  |  |  | Heating Angle |  |  |  | Heating Angle |  |  |  | Heating Angle |  |  |  | Heating Angle |  |  | Heating Angle |  |  | Heating Angle
deflection constant k | 0.00019341 |  |  | deflection constant k | 0.00037776 |  |  | deflection constant k | 0.00080884 |  |  | deflection constant k | 0.0018926 |  |  | deflection constant k | 0.0039417 |  |  | deflection constant k | 0.008227 |  |  | deflection constant k | 0.00075552 |  |  | deflection constant k | 0.0016177 |  |  | deflection constant k | 0.0037362 |  |  | deflection constant k | 0.0078834 |  | deflection constant k | 0.016454 |  | deflection constant k | #DIV/0!
Y penetration | -3.5 |  |  | Y penetration | -3.5 |  |  | Y penetration | -3.5 |  |  | Y penetration | -3.5 |  |  | Y penetration | -3.5 |  |  | Y penetration | -3.5 |  |  | Y penetration | -3.5 |  |  | Y penetration | -3.5 |  |  | Y penetration | -3.5 |  |  | Y penetration | -3.5 |  | Y penetration | -3.5 |  | Y penetration | -3.5
angle of depression case 1 |  |  |  | angle of depression case 1 |  |  |  | angle of depression case 1 |  |  |  | angle of depression case 1 |  |  |  | angle of depression case 1 |  |  |  | angle of depression case 1 |  |  |  | angle of depression case 1 |  |  |  | angle of depression case 1 |  |  |  | angle of depression case 1 |  |  |  | angle of depression case 1 |  |  | angle of depression case 1 |  |  | angle of depression case 1
Angle of Depression | -14.5928 | deg |  | Angle of Depression | -18.3568 | deg |  | Angle of Depression | -23.9485 | deg |  | Angle of Depression | -32.6079 | deg |  | Angle of Depression | -43.4869 | deg |  | Angle of Depression | -61.58 | deg |  | Angle of Depression | -23.3778 | deg |  | Angle of Depression | -30.7585 | deg |  | Angle of Depression | -42.5331 | deg |  | Angle of Depression | -60.1192 |  | Angle of Depression | #NUM! | deg | Angle of Depression | #DIV/0! | deg
Straight Path Length | 20.8377 | m |  | Straight Path Length | 16.6702 | m |  | Straight Path Length | 12.9337 | m |  | Straight Path Length | 9.7423 | m |  | Straight Path Length | 7.6287 | m |  | Straight Path Length | 5.9694 | m |  | Straight Path Length | 13.2311 | m |  | Straight Path Length | 10.2655 | m |  | Straight Path Length | 7.7661 | m |  | Straight Path Length | 6.0549 | m | Straight Path Length | #NUM! | m | Straight Path Length | #DIV/0! | m
X location of minimum | 20.1655 | m |  | X location of minimum | 15.8219 | m |  | X location of minimum | 11.8203 | m |  | X location of minimum | 8.2067 | m |  | X location of minimum | 5.5349 | m |  | X location of minimum | 2.841 | m |  | X location of minimum | 12.145 | m |  | X location of minimum | 8.8215 | m |  | X location of minimum | 5.7227 | m |  | X location of minimum | 3.0165 |  | X location of minimum | #NUM! | m | X location of minimum | #DIV/0! | m
satifies throw requirement | TRUE |  |  | satifies throw requirement | TRUE |  |  | satifies throw requirement | TRUE |  |  | satifies throw requirement | TRUE |  |  | satifies throw requirement | TRUE |  |  | satifies throw requirement | TRUE |  |  | satifies throw requirement | TRUE |  |  | satifies throw requirement | TRUE |  |  | satifies throw requirement | TRUE |  |  | satifies throw requirement | TRUE |  | satifies throw requirement | #NUM! |  | satifies throw requirement | #DIV/0!
angle of depression case 2 |  |  |  | angle of depression case 2 |  |  |  | angle of depression case 2 |  |  |  | angle of depression case 2 |  |  |  | angle of depression case 2 |  |  |  | angle of depression case 2 |  |  |  | angle of depression case 2 |  |  |  | angle of depression case 2 |  |  |  | angle of depression case 2 |  |  |  | angle of depression case 2 |  |  | angle of depression case 2 |  |  | angle of depression case 2
centreline distance | 24.2539 |  |  | centreline distance | 24.2539 |  |  | centreline distance | 24.2539 |  |  | centreline distance | 24.2539 |  |  | centreline distance | 24.2539 |  |  | centreline distance | 24.2539 |  |  | centreline distance | 24.2539 |  |  | centreline distance | 24.2539 |  |  | centreline distance | 24.2539 |  |  | centreline distance | 24.2539 |  | centreline distance | 24.2539 |  | centreline distance | 24.2539
compensated angle | -14.9563 |  |  | compensated angle | -21.5015 |  |  | compensated angle | -38.3241 |  |  | compensated angle | #NUM! |  |  | compensated angle | #NUM! |  |  | compensated angle | #NUM! |  |  | compensated angle | -36.0679 |  |  | compensated angle | #NUM! |  |  | compensated angle | #NUM! |  |  | compensated angle | #NUM! |  | compensated angle | #NUM! |  | compensated angle | #DIV/0!
direct angle | -8.2971 |  |  | direct angle | -8.2971 |  |  | direct angle | -8.2971 |  |  | direct angle | -8.2971 |  |  | direct angle | -8.2971 |  |  | direct angle | -8.2971 |  |  | direct angle | -8.2971 |  |  | direct angle | -8.2971 |  |  | direct angle | -8.2971 |  |  | direct angle | -8.2971 |  | direct angle | -8.2971 |  | direct angle | -8.2971
x distance ratio | 1.1902 |  |  | x distance ratio | 1.5169 |  |  | x distance ratio | 2.0304 |  |  | x distance ratio | 2.9244 |  |  | x distance ratio | 4.3361 |  |  | x distance ratio | 8.4476 |  |  | x distance ratio | 1.9761 |  |  | x distance ratio | 2.7206 |  |  | x distance ratio | 4.1938 |  |  | x distance ratio | 7.9561 |  | x distance ratio | #NUM! |  | x distance ratio | #DIV/0!
factored angle of depression | -16.2226 |  |  | factored angle of depression | -28.3266 |  |  | factored angle of depression | -69.2641 |  |  | factored angle of depression | #NUM! |  |  | factored angle of depression | #NUM! |  |  | factored angle of depression | #NUM! |  |  | factored angle of depression | -63.1758 |  |  | factored angle of depression | #NUM! |  |  | factored angle of depression | #NUM! |  |  | factored angle of depression | #NUM! |  | factored angle of depression | #NUM! |  | factored angle of depression | #DIV/0!
Heating Angle of Depression | -14.5928 |  |  | Heating Angle of Depression | -18.3568 |  |  | Heating Angle of Depression | -23.9485 |  |  | Heating Angle of Depression | -32.6079 |  |  | Heating Angle of Depression | -43.4869 |  |  | Heating Angle of Depression | -61.58 |  |  | Heating Angle of Depression | -23.3778 |  |  | Heating Angle of Depression | -30.7585 |  |  | Heating Angle of Depression | -42.5331 |  |  | Heating Angle of Depression | -60.1192 |  | Heating Angle of Depression | #NUM! |  | Heating Angle of Depression | #DIV/0!
Adjusted vs Cooling Angle | -14.5928 | degrees |  | Adjusted vs Cooling Angle | -18.3568 | degrees |  | Adjusted vs Cooling Angle | -23.9485 | degrees |  | Adjusted vs Cooling Angle | -32.6079 | degrees |  | Adjusted vs Cooling Angle | -43.4869 | degrees |  | Adjusted vs Cooling Angle | -61.58 | degrees |  | Adjusted vs Cooling Angle | -23.3778 | degrees |  | Adjusted vs Cooling Angle | -30.7585 | degrees |  | Adjusted vs Cooling Angle | -42.5331 | degrees |  | Adjusted vs Cooling Angle | -60.1192 | degrees | Adjusted vs Cooling Angle | #NUM! | degrees | Adjusted vs Cooling Angle | #DIV/0! | degrees
Heating distance | 20.8377 |  |  | Heating distance | 16.6702 |  |  | Heating distance | 12.9337 |  |  | Heating distance | 9.7423 |  |  | Heating distance | 7.6287 |  |  | Heating distance | 5.9694 |  |  | Heating distance | 13.2311 |  |  | Heating distance | 10.2655 |  |  | Heating distance | 7.7661 |  |  | Heating distance | 6.0549 |  | Heating distance | #NUM! |  | Heating distance | #DIV/0!
x location heat | 20.1655 |  |  | x location heat | 15.8219 |  |  | x location heat | 11.8203 |  |  | x location heat | 8.2067 |  |  | x location heat | 5.5349 |  |  | x location heat | 2.841 |  |  | x location heat | 12.145 |  |  | x location heat | 8.8215 |  |  | x location heat | 5.7227 |  |  | x location heat | 3.0165 |  | x location heat | #NUM! |  | x location heat | #DIV/0!
dT at Distance (heat) | 0.10366 |  |  | dT at Distance (heat) | 0.16197 |  |  | dT at Distance (heat) | 0.26906 |  |  | dT at Distance (heat) | 0.47422 |  |  | dT at Distance (heat) | 0.77339 |  |  | dT at Distance (heat) | 1.2631 |  |  | dT at Distance (heat) | 0.20406 |  |  | dT at Distance (heat) | 0.339 |  |  | dT at Distance (heat) | 0.59232 |  |  | dT at Distance (heat) | 0.97441 |  | dT at Distance (heat) | #NUM! |  | dT at Distance (heat) | #DIV/0!
Deflection (heat) | 2.8497 |  |  | Deflection (heat) | 5.5658 |  |  | Deflection (heat) | 11.9173 |  |  | Deflection (heat) | 27.8846 |  |  | Deflection (heat) | 58.0758 |  |  | Deflection (heat) | 121.214 |  |  | Deflection (heat) | 5.5658 |  |  | Deflection (heat) | 11.9173 |  |  | Deflection (heat) | 27.5241 |  |  | Deflection (heat) | 58.0758 |  | Deflection (heat) | 121.214 |  | Deflection (heat) | #DIV/0!
Arc of rotation | 9.473 | deg |  | Arc of rotation | 19.7074 | deg |  | Arc of rotation | 40.0265 | deg |  | Arc of rotation | 76.2451 | deg |  | Arc of rotation | 109.1552 | deg |  | Arc of rotation | 139.9115 | deg |  | Arc of rotation | 37.7095 | deg |  | Arc of rotation | 68.8823 | deg |  | Arc of rotation | 106.9136 | deg |  | Arc of rotation | 137.9349 | deg | Arc of rotation | #NUM! | deg | Arc of rotation | #DIV/0!
Can Thermal Adj | TRUE |  |  | Can Thermal Adj | TRUE |  |  | Can Thermal Adj | FALSE |  |  | Can Thermal Adj | FALSE |  |  | Can Thermal Adj | FALSE |  |  | Can Thermal Adj | FALSE |  |  | Can Thermal Adj | TRUE |  |  | Can Thermal Adj | FALSE |  |  | Can Thermal Adj | FALSE |  |  | Can Thermal Adj | FALSE |  | Can Thermal Adj | #NUM! |  | Can Thermal Adj | #DIV/0!
Can Electric Adj | TRUE |  |  | Can Electric Adj | TRUE |  |  | Can Electric Adj | TRUE |  |  | Can Electric Adj | FALSE |  |  | Can Electric Adj | FALSE |  |  | Can Electric Adj | FALSE |  |  | Can Electric Adj | TRUE |  |  | Can Electric Adj | FALSE |  |  | Can Electric Adj | FALSE |  |  | Can Electric Adj | FALSE |  | Can Electric Adj | #NUM! |  | Can Electric Adj | #DIV/0!
Mounting angle | 0 |  |  | Mounting angle | 0 |  |  | Mounting angle | 0 |  |  | Mounting angle | -2.6079 |  |  | Mounting angle | -13.4869 |  |  | Mounting angle | -31.58 |  |  | Mounting angle | 0 |  |  | Mounting angle | -0.7585 |  |  | Mounting angle | -12.5331 |  |  | Mounting angle | -30.1192 |  | Mounting angle | #NUM! |  | Mounting angle | #DIV/0!
Min Centreline Dist | 0.324 |  |  | Min Centreline Dist | 0.405 |  |  | Min Centreline Dist | 0.522 |  |  | Min Centreline Dist | 0.693 |  |  | Min Centreline Dist | 0.885 |  |  | Min Centreline Dist | 1.131 |  |  | Min Centreline Dist | 0.405 |  |  | Min Centreline Dist | 0.522 |  |  | Min Centreline Dist | 0.69 |  |  | Min Centreline Dist | 0.885 |  | Min Centreline Dist | 1.131 |  | Min Centreline Dist | 0.2592
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
| Results Collate | DN200 [S0] | DN250 [S0] | DN315 [S0] | DN400 [S0] | DN500 [S0] | DN630 [S0] | DN250 [S1] | DN315 [S1] | DN400 [S1] | DN500 [S1] | DN630 [S1]
1 | Airflow Rate | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
2 | Static Pressure | 279.2566 | 106.3755 | 39.6379 | 12.6707 | 4.4357 | 2.2559 | 169.6586 | 63.3517 | 20.3934 | 7.1894 | 3.6177
3 | Total Pressure Loss (Pa) | 304.0803 | 116.5433 | 43.6719 | 14.2222 | 5.0712 | 2.508 | 179.8264 | 67.3858 | 21.9449 | 7.8249 | 3.8698
4 | Permissible Pressure | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
5 | SWL (dB(A)) | 51.4893 | 34.1169 | 16.3895 | -3.3729 | -22.0037 | -34.1264 | 61.9124 | 50.1786 | 36.7088 | 24.1896 | 16.3219
6 | Throw (m) | 38.7122 | 30.9697 | 24.0282 | 18.0992 | 14.1726 | 11.09 | 16.7404 | 12.9882 | 9.8259 | 7.6609 | 5.9946
7 | Jet Velocity at Distance | 0.63164 | 0.50531 | 0.39205 | 0.29531 | 0.23124 | 0.18095 | 0.25808 | 0.20024 | 0.15148 | 0.1181 | 0.092416
8 | Jet dT at Distance (cool) | -0.088108 | -0.11014 | -0.14195 | -0.18845 | -0.24067 | -0.30756 | -0.055068 | -0.070976 | -0.093819 | -0.12033 | -0.15378
9 | Jet dT at Distance (heat) | 0.10366 | 0.16197 | 0.26906 | 0.47422 | 0.77339 | 1.2631 | 0.20406 | 0.339 | 0.59232 | 0.97441 | #NUM!
10 | Recommended Cooling Angle | -5.1198 | 1.3506 | 16.078 | 43.6372 | 65.6683 | 78.3316 | 14.3317 | 38.1238 | 64.3805 | 77.8157 | 84.228
11 | Recommended Heating Angle | -14.5928 | -18.3568 | -23.9485 | -32.6079 | -43.4869 | -61.58 | -23.3778 | -30.7585 | -42.5331 | -60.1192 | #NUM!
12 | Arc of Rotation | 9.473 | 19.7074 | 40.0265 | 76.2451 | 109.1552 | 139.9115 | 37.7095 | 68.8823 | 106.9136 | 137.9349 | #NUM!
13 | Mounting Angle | 0 | 0 | 0 | -2.6079 | -13.4869 | -31.58 | 0 | -0.7585 | -12.5331 | -30.1192 | #NUM!
14 | Min Centreline Dist | 0.324 | 0.405 | 0.522 | 0.693 | 0.885 | 1.131 | 0.405 | 0.522 | 0.69 | 0.885 | 1.131
15 | Area | 0.0091609 | 0.014314 | 0.023779 | 0.04191 | 0.068349 | 0.11163 | 0.014314 | 0.023779 | 0.041548 | 0.068349 | 0.11163
16 | Velocity | 21.832 | 13.9725 | 8.4109 | 4.7722 | 2.9261 | 1.7917 | 13.9725 | 8.4109 | 4.8138 | 2.9261 | 1.7917
17 | X dist heat location | 20.1655 | 15.8219 | 11.8203 | 8.2067 | 5.5349 | 2.841 | 12.145 | 8.8215 | 5.7227 | 3.0165 | #NUM!
18 | deflection k (cool) | -0.00019341 | -0.00037776 | -0.00080884 | -0.0018926 | -0.0039417 | -0.008227 | -0.00075552 | -0.0016177 | -0.0037362 | -0.0078834 | -0.016454
19 | deflection k (heat) | 0.00019341 | 0.00037776 | 0.00080884 | 0.0018926 | 0.0039417 | 0.008227 | 0.00075552 | 0.0016177 | 0.0037362 | 0.0078834 | 0.016454
| Results Format | DN200 [S0] | DN250 [S0] | DN315 [S0] | DN400 [S0] | DN500 [S0] | DN630 [S0] | DN250 [S1] | DN315 [S1] | DN400 [S1] | DN500 [S1] | DN630 [S1]
| Airflow Rate | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
| Static Pressure (Pa) | 279.3 | 106.4 | 39.6 | 12.7 | 4.4 | < 3 | 169.7 | 63.4 | 20.4 | 7.2 | 3.6
| Total Pressure (Pa) | 304.1 | 116.5 | 43.7 | 14.2 | 5.1 | < 3 | 179.8 | 67.4 | 21.9 | 7.8 | 3.9
| Permissible Pressure | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
| SWL (dB(A)) | 51.5 | 34.1 | 16.4 | < 4 | < 4 | < 4 | 61.9 | 50.2 | 36.7 | 24.2 | 16.3
| Throw (m) | 38.7 | 31 | 24 | 18.1 | 14.2 | 11.1 | 16.7 | 13 | 9.8 | 7.7 | 6
| Jet Velocity at Distance | 0.63 | 0.51 | 0.39 | 0.3 | 0.23 | 0.18 | 0.26 | 0.2 | 0.15 | 0.12 | 0.09
| Jet dT at Distance (cool) | -0.1 | -0.1 | -0.1 | -0.2 | -0.2 | -0.3 | -0.1 | -0.1 | -0.1 | -0.1 | -0.2
| Jet dT at Distance (heat) | 0.1 | 0.2 | 0.3 | 0.5 | 0.8 | 1.3 | 0.2 | 0.3 | 0.6 | 1 | #NUM!
| Recommended Cooling Angle | -5 | 1 | 16 | 44 | 66 | 78 | 14 | 38 | 64 | 78 | 84
| Recommended Heating Angle | -15 | -18 | -24 | -33 | -43 | -62 | -23 | -31 | -43 | -60 | #NUM!
| Arc of Rotation | 9 | 20 | 40 | 76 | 109 | 140 | 38 | 69 | 107 | 138 | #NUM!
| Mounting Angle | 0 | 0 | 0 | -3 | -13 | -32 | 0 | -1 | -13 | -30 | #NUM!
| Min Centreline Dist | 0.32 | 0.41 | 0.52 | 0.69 | 0.89 | 1.13 | 0.41 | 0.52 | 0.69 | 0.89 | 1.13
| Duct Diameter | 630 | 500 | 400 | 315 | 250 | 200 | 200 | 200 | 200 | 200 | 200
| Exit Diameter | 337 | 277 | 230 | 174 | 136 | 108 | 108 | 108 | 108 | 108 | 108
|  | 1 | 2 | 3 | 4 | 5 | 6
| Results Validation | DN200 [S0] | DN250 [S0] | DN315 [S0] | DN400 [S0] | DN500 [S0] | DN630 [S0]
| Selected Airflow Rate [L/s] | 200 | 200 | 200 | 200 | 200 | 200
| Static Pressure @ Airflow [Pa] | 279.3 | 106.4 | 39.6 | 12.7 | 4.4 | < 3
| Total Pressure @ Airflow [Pa] | 304.1 | 116.5 | 43.7 | 14.2 | 5.1 | < 3
| Max Selected Pressure [Pa] | 60 | 60 | 60 | 60 | 60 | 60
| SWL | 51.5 | 34.1 | 16.4 | < 4 | < 4 | < 4
| Max Throw Distance [m] | 38.7 | 31 | 24 | 18.1 | 14.2 | 11.1
| Jet Velocity at 24m | 0.63 | 0.51 | 0.39 | 0.3 | 0.23 | 0.18
| Jet ΔT at 24 m (cooling) | -0.1 | -0.1 | -0.1 | -0.2 | -0.2 | -0.3
| Jet ΔT at 24 m (heating) | 0.1 | 0.2 | 0.3 | 0.5 | 0.8 | 1.3
| Recommended Cooling Angle | -5 | 1 | 16 | 44 | 66 | 78
| Recommended Heating Angle | -15 | -18 | -24 | -33 | -43 | -62
| Arc of Rotation | 9 | 20 | 40 | 76 | 109 | 140
| Mounting Angle | 0 | 0 | 0 | -3 | -13 | -32
| Min Centreline Dist | 0.32 | 0.41 | 0.52 | 0.69 | 0.89 | 1.13
| Duct Diameter | 630 | 500 | 400 | 315 | 250 | 200
| Exit Diameter | 337 | 277 | 230 | 174 | 136 | 108
| Results Units | DN200 [S0] | DN250 [S0] | DN315 [S0] | DN400 [S0] | DN500 [S0] | DN630 [S0]
| Selected Airflow Rate [L/s] | 200 | 200 | 200 | 200 | 200 | 200
| Static Pressure @ Airflow [Pa] | 279.3 | 106.4 | 39.6 | 12.7 | 4.4 | < 3
| Total Pressure @ Airflow [Pa] | 304.1 | 116.5 | 43.7 | 14.2 | 5.1 | < 3
| Max Selected Pressure [Pa] | 60 | 60 | 60 | 60 | 60 | 60
| SWL | 51.5 | 34.1 | 16.4 | < 4 | < 4 | < 4
| Max Throw Distance [m] | 38.7 | 31 | 24 | 18.1 | 14.2 | 11.1
| Jet Velocity at 24m | 0.63 | 0.51 | 0.39 | 0.3 | 0.23 | 0.18
| Jet ΔT at 24 m (cooling) | -0.1 | -0.1 | -0.1 | -0.2 | -0.2 | -0.3
| Jet ΔT at floor level (heating) | 0.1 | 0.2 | 0.3 | 0.5 | 0.8 | 1.3
| Recommended Cooling Angle | -5 | 1 | 16 | 44 | 66 | 78
| Recommended Heating Angle | -15 | -18 | -24 | -33 | -43 | -62
| Arc of Rotation | 9 | 20 | 40 | 76 | 109 | 140
| Mounting Angle | 0 | 0 | 0 | -3 | -13 | -32
| Min Centreline Dist | 0.32 | 0.41 | 0.52 | 0.69 | 0.89 | 1.13
| Duct Diameter | 630 | 500 | 400 | 315 | 250 | 200
| Exit Diameter | 337 | 277 | 230 | 174 | 136 | 108
Colour Formatting
| Pressure | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE
| Low Pressure | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE
| Diagonal Throw Dist Error | 59.1% | 27.02% | 2.147% | 26.73% | 42.98% | 55.9%
| Throw Distance Highlight | R | R | FALSE | R | R | R
| Warning Shade | 1: Throw Distance Highlight; 2: 0
| Cooling Angle | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
| Heating Angle | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE
| Arc angle | [6 empty] | TRUE | bar: 1 to 6
| grey | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE
| excess velocity | R | O | B | B | B | B | Velocity Limit | 0.46 | 0.56
FLOW PROFILE
Selection
0
1 | Airflow Rate | 1: Airflow Rate
2 | Static Pressure | 1: Static Pressure
3 | Total Pressure Loss (Pa) | 1: Total Pressure Loss (Pa)
4 | Permissible Pressure | 1: Permissible Pressure
5 | SWL (dB(A)) | 1: SWL (dB(A))
6 | Throw (m) | 1: Throw (m)
7 | Jet Velocity at Distance | 1: Jet Velocity at Distance
8 | Jet dT at Distance (cool) | 1: Jet dT at Distance (cool)
9 | Jet dT at Distance (heat) | 1: Jet dT at Distance (heat)
10 | Recommended Cooling Angle | 1: 0
11 | Recommended Heating Angle | 1: 0
12 | arc of rotation | 1: Arc of Rotation
13 | mounting angle | 1: Mounting Angle
14 | Min Centreline Dist | 1: Min Centreline Dist
15 | Area | 1: Area
16 | Velocity | 1: Velocity
17 | X heat location | 1: X dist heat location
18 | deflection k cool | 1: deflection k (cool)
19 | deflection k heat | 1: deflection k (heat)
Cool
|  | X | 24 | 0 | 2 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 26 | 28 | 30 | 32 | 36 | 40 | 44 | 48 | 52 | 56 | 60 | 65 | 70 | 75 | 80 | 85 | 90 | 95 | 100
|  | Diagonal Y | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | L | 24 |  | 2 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 26 | 28 | 30 | 32 | 36 | 40 | 44 | 48 | 52 | 56 | 60 | 65 | 70 | 75 | 80 | 85 | 90 | 95 | 100
|  | Actual Y | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Heat
|  | X | X dist heat location | 0 | 2 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 26 | 28 | 30 | 32 | 36 | 40 | 44 | 48 | 52 | 56 | 60 | 65 | 70 | 75 | 80 | 85 | 90 | 95 | 100
|  | Direct Y | #VALUE! |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | L | #VALUE! |  | 2 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 26 | 28 | 30 | 32 | 36 | 40 | 44 | 48 | 52 | 56 | 60 | 65 | 70 | 75 | 80 | 85 | 90 | 95 | 100
|  | Actual Y | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Selected Data
|  | Discharge | 0 | 5
Cooling
|  | X | 24 | 0 | 2 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Y | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Heating
|  | X | X dist heat location | 0 | 2 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 26 | 28 | 30 | 32 | 36 | 40 | 44 | 48 | 52 | 56 | 60 | 65 | 70 | 75 | 80 | 85 | 90 | 95 | 100
|  | Y | #VALUE! | 5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!

## Notes
SMARTEMP PRODUCT SELECTION CALCULATOR
Circular Nozzle [CNW-AD] Notes
Dimensions
Select Unit Size | DN250
|  | 1 | D3 | 248 | D3 = 248
|  | 2 | D1 | 136 | D1 = 136
|  | 3 | D2 | 302 | D2 = 302
|  | 4 | L | 164 | L = 164
|  | 5 | E | 24 | E = 24
|  | 6 | LE | 340 | Le = 340
ALL DIMENSIONS IN mm
Minimum Centreline Distance
Minimum Spacing Between Nozzles |  | DN200 | DN250 | DN315 | DN400 | DN500 | DN630
min centreline distance [m] | without swirl [S0] | 0.32 | 0.41 | 0.52 | 0.69 | 0.89 | 1.13
| with swirl [S1] | - | 0.54 | 0.7 | 0.92 | 1.18 | 1.51
D3 = 248
D1 = 136
D2 = 302
L = 164
E = 24
Le = 340

## CNW-AD Data (hidden)
| Selection Button | 0
| Selection | 0
0 |  | Results Units
1 | Selected Airflow Rate [L/s] | Selected Airflow Rate [L/s]
2 | Static Pressure @ Airflow [Pa] | Static Pressure @ Airflow [Pa]
3 | Total Pressure @ Airflow [Pa] | Total Pressure @ Airflow [Pa]
4 | Max Selected Pressure [Pa] | Max Selected Pressure [Pa]
5 | SWL | SWL
6 | Max Throw Distance [m] | Max Throw Distance [m]
7 | Jet Velocity at 20m | Jet Velocity at 24m
8 | Jet ΔT at 20 m (cooling) | Jet ΔT at 24 m (cooling) | +Jet ΔT at 24 m (cooling)
9 | Jet ΔT at floor level (heating) | Jet ΔT at floor level (heating) | +Jet ΔT at floor level (heating)
10 | Recommended Cooling Angle | Recommended Cooling Angle | +Recommended Cooling Angle
11 | Recommended Heating Angle | Recommended Heating Angle | +Recommended Heating Angle
12 | Arc of Rotation | Arc of Rotation
13 | Mounting Angle | Mounting Angle | +Mounting Angle
14 | Min Centreline Dist | Min Centreline Dist
15 | Duct Diameter | Duct Diameter
16 | Exit Diameter | Exit Diameter
Input
| Distance Selected | 24
| Cooling | -6
| heating | 6 | +6
SELECTION
| Available Sizes | 1 | 2 | 3 | 4 | 5 | 6 | 0
|  | DN200 | DN250 | DN315 | DN400 | DN500 | DN630 | N/A | DN630 | DN500 | DN400 | DN315 | DN250 | DN200
| Selection Data | DN200 | DN250 | DN315 | DN400 | DN500 | DN630 | N/A
| Size | 1: N/A; 2: N/A
Swirl | bar: 1
| Adjustment | 2: Adjustments
| 0 | 2: M; 3: E; 4: T
| 1 | DN200 | M | E | T |  | M | Manual
| 2 | DN250 | M | E | T |  | E | Electric Motor
| 3 | DN315 | M | E | T |  | T | Thermal Element
| 4 | DN400 | M | E | T |  | <N/A> | Not Available
| 5 | 1: DN500; 2: M; 3: E; 4: T
| 6 | 1: DN630; 2: M; 3: E; 4: T
| 0 | 1: 0; 2: M; 3: E; 4: T
|  |  | Manual | Electric Motor | Thermal Element
| Adjustment Selection | 1: 1; 2: M; 3: Manual
| Max Arc | 1: 60
| Warning Highlight | 1: TRUE
| Colour | 1: 1; 2: RAL9003; 3: RAL9003 - Signal White
|  | 2 | RAL9005 | RAL9005 - Jet Black
|  | 3 | <colour> | custom colour
| Selection | 1: 1; 2: RAL9003; 3: RAL9003 - Signal White
| Code | 1: please select a valid size in row 41
Summary
| Size and model | 1: please select a valid size on CNW-AD page
| Selected Airflow | 2: Selected Airflow Rate [L/s] L/s @ Static Pressure @ Airflow [Pa] Pa static (Total Pressure @ Airflow [Pa] Pa total)
| Selected throw distance | 2: 24 m (Max Throw Distance [m] m recommended @ Selected Airflow Rate [L/s]L/s)
| Centreline velocity | 2: Jet Velocity at 24m m/s at 24 m from discharge
| cool temp | 2: ΔT = +Jet ΔT at 24 m (cooling) K at 24 m
| heat temp | 2: ΔT = +Jet ΔT at floor level (heating) K at occupancy level
| Sound Power Level | 1: SWL dB(A)
Discharge
| Cooling | 1: +Recommended Cooling Angle° recommended discharge angle for cooling at ΔT = -6 K (relative to horizontal)
| Heating | 1: +Recommended Heating Angle° recommended discharge angle for heating at ΔT = +6 K (relative to horizontal)
| Angle | 1: +Mounting Angle ° recommended face mounting angle (relative to vertical)
Nozzle Configuration
| Size | 1: Nozzle diffuser with neck size N/A mm
No swirl element
Manual direction adjustment
Powder coated to RAL9003 - Signal White
Diagram
Velocity Profile
| Exit Diameter | 1: #VALUE!
| Area | 1: #VALUE!
| Velocity | 1: #VALUE!
Jet Velocity
| 0.25D | 1: 6; 2: #VALUE!
| 0.5D | 1: 12; 2: #VALUE!
| 0.75D | 1: 18; 2: #VALUE!
| 1D | 1: 24; 2: #VALUE!
Deflection Profile
| Straight Throw Distance | 1: 24
| Total Angle | 1: #REF!; 2: Rad
| Throw Height | 1: #REF!
| Throw Distance | 1: #REF!
Cooling
| Deflection Height | 1: #REF!
| Distance | 1: #REF!
Heating
| Deflection Height | 1: #REF!
| Distance | 1: #REF!

## CNW-ADsizing (hidden)
DN200
DN250
DN315
DN400
DN500
DN630
| DN200 | DN250 | DN315 | DN400 | DN500 | DN630
D3 | 198 | 248 | 313 | 398 | 498 | 628
D1 | 108 | 136 | 174 | 230 | 295 | 377
D2 | 257 | 302 | 384 | 467 | 600 | 733
L | 140 | 164 | 177 | 194 | 258 | 240
E | 20 | 24 | 24 | 24 | 28 | 32
Le | N/A | 340 | 340 | 340 | 415 | 460

## Selection Summary
CNW-AD Performance Calculator Summary
Project | <Project Name>
Company | <Name>
Consultant | <Name>
Product | SMARTEMP CNW-AD Adjustable Nozzle
Size | please select a valid size on CNW-AD page
Summary
Selected Airflow
Selected Throw Distance
Centreline Velocity
Tcentreline - Troom for Cooling
Tcentreline - Troom for Heating
Acoustic Performance
Sound Power Level ¹ | SWL dB(A) | ¹ Valid for manual adjustment
Recommended Discharge Settings
Configuration | Nozzle diffuser with neck size N/A mm
No swirl element
Manual direction adjustment
Powder coated to RAL9003 - Signal White
Order Code | please select a valid size in row 41
+Recommended Cooling Angle° recommended discharge angle for cooling at ΔT = -6 K (relative to horizontal)
+Recommended Heating Angle° recommended discharge angle for heating at ΔT = +6 K (relative to horizontal)
+Mounting Angle ° recommended face mounting angle (relative to vertical)