## ASF-AD
SMARTEMP PRODUCT SELECTION CALCULATOR
Auditorium Floor Swirl Diffuser [ASF-AD]
Inputs | [8 empty] | v 2.0 [08/2017]
Airflow Rate | 12 | L/s | m3/h
Maximum Permissible Pressure | 20 | Pa | default 20 Pa
| Basket A1 | For assembly halls with non-critical acoustical criteria, such as lecture theatres.
| Basket A2 | For acoustically stringent assembly halls such as opera houses.
Results
Damper Setting | 100% | 80% | 60% | 40% | 20%
Sound Power Level (dB(A)) | 17.2837 | 19.8805 | 25.2239 | 34.8259 | 55.7316
Sound Pressure Level (dB(A)) * | 28.2837 | 30.8805 | 36.2239 | 45.8259 | 66.7316
Sound Pressure Level (NC) * | 21.7283 | 24.1872 | 32.0583 | 43.748 | 65.9422 | Key: | Suitable | Not Suitable
Total Pressure Loss (Pa) | 7.2547 | 10.0354 | 16.344 | 32.608 | 118.9119 | * | Refer to 'ASF-AD Acoustic Data' worksheet for detailed acoustic data
Max Permissible Pressure Loss (Pa) | 20 | 20 | 20 | 20 | 20 |  | Estimated sound pressure level for seated occupant based on one
diffuser per seat
Product Selection & Code Generator
Material |  | Polycarbonate * |  | Aluminium
Basket 1 |  | As selected *(cell D12) |  | No basket |  |  |  | 1 only with mounting ring
Dampers 2 |  | No damper |  | Damper *3 |  |  |  | 2 only with basket
Mounting Ring |  | No mounting ring |  | With rubber collar * |  | With claw fastener 4 |  | 3 damper to be set on-site (by others)
Colour |  | ST * (standard grey/alu) |  | RAL9005 (jet black) |  | custom ^ |  | 4 only available with aluminium ring
Connection |  | No connection * |  | Connection box |  |  |  | ^ contact Smartair for custom colours
Product Code | SMARTEMP ASF-AD-P-DN200-BA1-DD-RR-ST-O | [6 empty] | * indicates standard/default option
|  | click to see product on smartair.asia |  |  |  |  | Copyright © 2017 SMARTAIR DIFFUSION
Group Box 21
Group Box 24
Group Box 27
Group Box 30
Group Box 35
Group Box 40
Group Box 43
sd

## ASF-ADequations (hidden)
Units
Units Type | 1
Units multiplier | 1
Input Values
Airflow Rate | 12 |  |  | 2.4L/s | 20
Max Pressure | 20
Basket | 1 | A1
A1 | 100% | [6 empty] | A1 | 80% | [6 empty] | A1 | 60% |  |  |  | A1 | 40% |  |  |  | A1 | 20% | [5 empty] | A2 | 100% |  |  |  | A2 | 80% |  |  |  | A2 | 60% |  |  |  | A4 | 40%
SWL (dB(A)) | 17.2837 | [6 empty] | SWL | 19.8805 | [6 empty] | SWL | 25.2239 |  |  |  | SWL | 34.8259 |  |  |  | SWL | 55.7316 | [5 empty] | SWL | 10.5857 |  |  |  | SWL | 19.8507 |  |  |  | SWL | 23.1186 |  |  |  | SWL | 30.0967
SPL (dB(A)) | [7 empty] | SPL (dB(A)) | [7 empty] | SPL (dB(A)) |  |  |  |  | SPL (dB(A)) |  |  |  |  | SPL (dB(A)) | [6 empty] | SPL (dB(A)) |  |  |  |  | SPL (dB(A)) |  |  |  |  | SPL (dB(A)) |  |  |  |  | SPL (dB(A))
SPL (NC) | 21.7283 | [6 empty] | SPL (NC) | 24.1872 | [6 empty] | SPL (NC) | 32.0583 |  |  |  | SPL (NC) | 43.748 |  |  |  | SPL (NC) | 65.9422 | [5 empty] | SPL (NC) | 14.7269 |  |  |  | SPL (NC) | 26.5063 |  |  |  | SPL (NC) | 29.7624 |  |  |  | SPL (NC) | 36.6558
Total Pressure Loss (Pa) | 7.2547 |  | 12 | 16.67 | 14 |  |  | Total Pressure Loss (Pa) | 10.0354 |  | 15 | 17.7169 | 14 |  |  | Total Pressure Loss (Pa) | 16.344 | 20 | 18.5104 | 14 | Total Pressure Loss (Pa) | 32.608 | 30 | 19.6573 | 14 | Total Pressure Loss (Pa) | 118.9119 | 60 | 20.5875 | 14 |  |  | Total Pressure Loss (Pa) | 9.8649 | 12 | 15.2825 | 16 | Total Pressure Loss (Pa) | 13.6474 | 12 | 12.9932 | 16 | Total Pressure Loss (Pa) | 22.2237 | 12 | 10.182 | 16 | Total Pressure Loss (Pa) | 44.3372 | 12 | 7.2087 | 16
|  |  |  | V | P
[9 empty] | 14.1137 |  |  | 16.67 |  |  |  |  | 10.8069 |  | 16.67 |  |  | 10.1764 |  | 16.67 |  |  | 9.7166 |  | 16.67 |  |  |  |  | Q
[31 empty] | P | 5 |  | 8.5432 |  |  |  | 5 | 7.2634 |  |  |  | 5 | 5.6919 |  |  |  | 5 | 4.0298
| 100% | 80% | 60% | 40% | 20% | [26 empty] | 10 |  | 12.0819 |  |  |  | 10 | 10.272 |  |  |  | 10 | 8.0496 |  |  |  | 10 | 5.699
| 100% | 80% | 60% | 40% | [27 empty] | 15 |  | 14.7972 |  |  |  | 15 | 12.5806 |  |  |  | 15 | 9.8587 |  |  |  | 15 | 6.9798
Results | 100% | 80% | 60% | 40% | 20% | [26 empty] | 20 |  | 17.0864 |  |  |  | 20 | 14.5268 |  |  |  | 20 | 11.3838 |  |  |  | 20 | 8.0596
SWL (dB(A)) | 17.2837 | 19.8805 | 25.2239 | 34.8259 | 55.7316 | [26 empty] | 25 |  | 19.1031 |  |  |  | 25 | 16.2415 |  |  |  | 25 | 12.7275 |  |  |  | 25 | 9.0109
SPL (dB(A)) | 28.2837 | 30.8805 | 36.2239 | 45.8259 | 66.7316 | [26 empty] | 30 |  | 20.9264 |  |  |  | 30 | 17.7917 |  |  |  | 30 | 13.9423 |  |  |  | 30 | 9.8709
SPL (NC) | 21.7283 | 24.1872 | 32.0583 | 43.748 | 65.9422
Total Pressure Loss (Pa) | 7.2547 | 10.0354 | 16.344 | 32.608 | 118.9119 | [26 empty] | 80 |  | 34.1727 |  |  |  | 80 | 29.0537 |  |  |  | 80 | 22.7676 |  |  |  | 80 | 16.1191
Max pressure | 20 | 20 | 20 | 20 | 20
Acoustic A1 | [11 empty] | S Pressure L
| A*LOG | 8.7273 | 10.441 | 9.8138 | 18.981
| +B | 2.9783 | -3.4927 | -2.1067 | -28.027 | 5 | 5 | [7 empty] | dB |  | SPL
| P | 125 | 250 | 500 | 1000 | 2000 | 4000 | SWL |  |  | 125 | 250 | 500 | 1000 | 2000 | 4000
100% | 7.2547 | 20.2727 | 17.1977 | 17.3408 | 9.5867 | 5 | 5 |  |  | 100% | 31.2727 | 28.1977 | 28.3408 | 20.5867 | 16 | 16
80% | 10.0354 | 22.1354 | 19.6164 | 19.556 | 14.7764 | 4.0309 | 4.0309 |  |  | 80% | 33.1354 | 30.6164 | 30.556 | 25.7764 | 15.0309 | 15.0309
60% | 16.344 | 25.1427 | 23.4595 | 23.0932 | 22.7848 | 2.7815 | 2.7815 |  |  | 60% | 36.1427 | 34.4595 | 34.0932 | 33.7848 | 13.7815 | 13.7815
40% | 32.608 | 29.4097 | 28.9102 | 28.1107 | 34.134 | 1.0206 | 1.0206 |  |  | 40% | 40.4097 | 39.9102 | 39.1107 | 45.134 | 12.0206 | 12.0206
20% | 118.9119 | 37.691 | 39.4087 | 37.7977 | 55.6818 | -1.9897 | -1.9897 |  |  | 20% | 48.691 | 50.4087 | 48.7977 | 66.6818 | 9.0103 | 9.0103
|  | -16 | -9 | -3 | 0 | 1 | 1 |  |  |  | -16 | -9 | -3 | 0 | 1 | 1
[8 empty] | dBA | [6 empty] | dBA |  | dBA
| 100% | 4.2727 | 8.1977 | 14.3408 | 9.5867 | 6 | 6 | 17.2837 |  | 100% | 15.2727 | 19.1977 | 25.3408 | 20.5867 | 17 | 17 | 28.2837
| 80% | 6.1354 | 10.6164 | 16.556 | 14.7764 | 5.0309 | 5.0309 | 19.8805 |  | 80% | 17.1354 | 21.6164 | 27.556 | 25.7764 | 16.0309 | 16.0309 | 30.8805
| 60% | 9.1427 | 14.4595 | 20.0932 | 22.7848 | 3.7815 | 3.7815 | 25.2239 |  | 60% | 20.1427 | 25.4595 | 31.0932 | 33.7848 | 14.7815 | 14.7815 | 36.2239
| 40% | 13.4097 | 19.9102 | 25.1107 | 34.134 | 2.0206 | 2.0206 | 34.8259 |  | 40% | 24.4097 | 30.9102 | 36.1107 | 45.134 | 13.0206 | 13.0206 | 45.8259
| 20% | 21.691 | 30.4087 | 34.7977 | 55.6818 | -0.9897 | -0.9897 | 55.7316 |  | 20% | 32.691 | 41.4087 | 45.7977 | 66.6818 | 10.0103 | 10.0103 | 66.7316
[11 empty] | 125 | 250 | 500 | 1000 | 2000 | 4000 | NC
|  | 125 | 250 | 500 | 1000 | 2000 | 4000 |  |  | 100% | 6.9873 | 13.6372 | 21.7283 | 18.4643 | 16.6 | 19.15 | 21.7283
Validation | 100% | 20.2727 | 17.1977 | 17.3408 | 9.5867 | 5 | 5 |  |  | 80% | 9.4274 | 16.5397 | 24.1872 | 23.8097 | 15.6309 | 18.21 | 24.1872
| 80% | 22.1354 | 19.6164 | 19.556 | 14.7764 | 4.0309 | 4.0309 |  |  | 60% | 13.3669 | 21.1514 | 28.1134 | 32.0583 | 14.3815 | 16.9981 | 32.0583
| 60% | 25.1427 | 23.4595 | 23.0932 | 22.7848 | 2.7815 | 2.7815 |  |  | 40% | 18.9567 | 27.6922 | 33.6828 | 43.748 | 12.6206 | 15.29 | 43.748
| 40% | 29.4097 | 28.9102 | 28.1107 | 34.134 | 1.0206 | 1.0206 |  |  | 20% | 29.8052 | 40.2904 | 44.4354 | 65.9422 | 9.6103 | 12.37 | 65.9422
| 20% | 37.691 | 39.4087 | 37.7977 | 55.6818 | 0 | 0
Display | 100% | 20.2727 | 17.1977 | 17.3408 | 9.5867 | <5 | <5
| 80% | 22.1354 | 19.6164 | 19.556 | 14.7764 | <5 | <5
| 60% | 25.1427 | 23.4595 | 23.0932 | 22.7848 | <5 | <5
| 40% | 29.4097 | 28.9102 | 28.1107 | 34.134 | <5 | <5
| 20% | 37.691 | 39.4087 | 37.7977 | 55.6818 | <5 | <5
Acoustic A2 | [7 empty] | SWL
| P | 125 | 250 | 500 | 1000 | 2000 | 4000 | dB | [6 empty] | dB |  | SPL
100 | 9.8649 | 12.8117 | 11.4798 | 7.1785 | 5.9582 | 2.7832 | -7.1262 |  |  |  | 23.8117 | 22.4798 | 18.1785 | 16.9582 | 13.7832 | 3.8738
80 | 13.6474 | 6.9523 | 15.3569 | 12.8154 | 16.3345 | 14.9063 | -3.006 |  |  |  | 17.9523 | 26.3569 | 23.8154 | 27.3345 | 25.9063 | 7.994
60 | 22.2237 | 17.5012 | 19.5012 | 17.4757 | 18.9622 | 18.1624 | 4.0265 |  |  |  | 28.5012 | 30.5012 | 28.4757 | 29.9622 | 29.1624 | 15.0265
40 | 44.3372 | 23.0268 | 25.0268 | 24.5755 | 25.8941 | 25.0558 | 15.2244 |  |  |  | 34.0268 | 36.0268 | 35.5755 | 36.8941 | 36.0558 | 26.2244
|  | -16 | -9 | -3 | 0 | 1 | 1 |  |  |  | -16 | -9 | -3 | 0 | 1 | 1
[8 empty] | dBA | [6 empty] | dBA |  | dBA
| 100% | -3.1883 | 2.4798 | 4.1785 | 5.9582 | 3.7832 | -6.1262 | 10.5857 |  |  | 7.8117 | 13.4798 | 15.1785 | 16.9582 | 14.7832 | 4.8738 | 21.5857
| 80% | -9.0477 | 6.3569 | 9.8154 | 16.3345 | 15.9063 | -2.006 | 19.8507 |  |  | 1.9523 | 17.3569 | 20.8154 | 27.3345 | 26.9063 | 8.994 | 30.8507
| 60% | 1.5012 | 10.5012 | 14.4757 | 18.9622 | 19.1624 | 5.0265 | 23.1186 |  |  | 12.5012 | 21.5012 | 25.4757 | 29.9622 | 30.1624 | 16.0265 | 34.1186
| 40% | 7.0268 | 16.0268 | 21.5755 | 25.8941 | 26.0558 | 16.2244 | 30.0967 |  |  | 18.0268 | 27.0268 | 32.5755 | 36.8941 | 37.0558 | 27.2244 | 41.0967
Validation |  | 125 | 250 | 500 | 1000 | 2000 | 4000 |  |  |  | 125 | 250 | 500 | 1000 | 2000 | 4000 | NC
100 | 9.8649 | 12.8117 | 11.4798 | 7.1785 | 5.9582 | 2.7832 | 0 |  |  | 100% | -2.7867 | 6.7757 | 10.4482 | 14.7269 | 14.3832 | 7.3876 | 14.7269
80 | 13.6474 | 6.9523 | 15.3569 | 12.8154 | 16.3345 | 14.9063 | 0 |  |  | 80% | -10.4625 | 11.4283 | 16.7051 | 25.4145 | 26.5063 | 11.3842 | 26.5063
60 | 22.2237 | 17.5012 | 19.5012 | 17.4757 | 18.9622 | 18.1624 | 4.0265 |  |  | 60% | 3.3566 | 16.4015 | 21.878 | 28.1211 | 29.7624 | 18.2057 | 29.7624
40 | 44.3372 | 23.0268 | 25.0268 | 24.5755 | 25.8941 | 25.0558 | 15.2244 |  |  | 40% | 10.595 | 23.0321 | 29.7588 | 35.2609 | 36.6558 | 29.0677 | 36.6558
Display | 100% | 12.8117 | 11.4798 | 7.1785 | 5.9582 | <5 | <5
| 80% | 6.9523 | 15.3569 | 12.8154 | 16.3345 | 14.9063 | <5
| 60% | 17.5012 | 19.5012 | 17.4757 | 18.9622 | 18.1624 | <5
| 40% | 23.0268 | 25.0268 | 24.5755 | 25.8941 | 25.0558 | 15.2244
| 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
NC 15 | 47 | 36 | 29 | 22 | 17 | 14 | 12 | 11
NC 20 | 51 | 41 | 33 | 26 | 22 | 19 | 17 | 16
NC 25 | 54 | 45 | 38 | 31 | 27 | 24 | 22 | 21
NC 30 | 57 | 48 | 41 | 35 | 31 | 29 | 28 | 27
NC 35 | 60 | 53 | 46 | 40 | 36 | 34 | 33 | 32
Product Selection
Radio
material | 1 | P | Polycarbonate
basket | 1 | A1 | A1
damper | 2 | D | With Damper
mounting ring | 2 | R | With rubber collar
colour | 1 | ST | Standard grey/alu finish
connection | 1 | O | No connection
Code | SMARTEMP ASF-AD-P-DN200-BA1-DD-RR-ST-O

## ASF-AD Acoustic Data
SMARTEMP PRODUCT SELECTION CALCULATOR
Auditorium Floor Swirl Diffuser [ASF-AD] Acoustic Data
Basket A1 | [6 empty] | Basket A2
| 125 | 250 | 500 | 1000 | 2000 | 4000
| 31.2727 | 28.1977 | 28.3408 | 20.5867 | 16 | 16 |  | 23.8117 | 22.4798 | 18.1785 | 16.9582 | 13.7832 | 3.8738
Basket A1 100% Setting | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | Basket A2 100% Setting | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz
Sound Power Level (dB) | 20.2727 | 17.1977 | 17.3408 | 9.5867 | <5 | <5 | Sound Power Level (dB) | 12.8117 | 11.4798 | 7.1785 | 5.9582 | <5 | <5
Sound Power Level [dB(A)] | 17.2837 | [5 empty] | Sound Power Level [dB(A)] | 10.5857
Sound Pressure Level [dB(A)] | 28.2837 | [5 empty] | Sound Pressure Level [dB(A)] | 21.5857
Sound Pressure Level [NC] | 21.7283 | [5 empty] | Sound Pressure Level [NC] | 14.7269
| 33.1354 | 30.6164 | 30.556 | 25.7764 | 15.0309 | 15.0309 |  | 17.9523 | 26.3569 | 23.8154 | 27.3345 | 25.9063 | 7.994
Basket A1 80% Setting | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | Basket A2 80% Setting | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz
Sound Power Level (dB) | 22.1354 | 19.6164 | 19.556 | 14.7764 | <5 | <5 | Sound Power Level (dB) | 6.9523 | 15.3569 | 12.8154 | 16.3345 | 14.9063 | <5
Sound Power Level [dB(A)] | 19.8805 | [5 empty] | Sound Power Level [dB(A)] | 19.8507
Sound Pressure Level [dB(A)] | 30.8805 | [5 empty] | Sound Pressure Level [dB(A)] | 30.8507
Sound Pressure Level [NC] | 24.1872 | [5 empty] | Sound Pressure Level [NC] | 26.5063
| 36.1427 | 34.4595 | 34.0932 | 33.7848 | 13.7815 | 13.7815 |  | 28.5012 | 30.5012 | 28.4757 | 29.9622 | 29.1624 | 15.0265
Basket A1 60% Setting | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | Basket A2 60% Setting | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz
Sound Power Level (dB) | 25.1427 | 23.4595 | 23.0932 | 22.7848 | <5 | <5 | Sound Power Level (dB) | 17.5012 | 19.5012 | 17.4757 | 18.9622 | 18.1624 | <5
Sound Power Level [dB(A)] | 25.2239 | [5 empty] | Sound Power Level [dB(A)] | 23.1186
Sound Pressure Level [dB(A)] | 36.2239 | [5 empty] | Sound Pressure Level [dB(A)] | 34.1186
Sound Pressure Level [NC] | 32.0583 | [5 empty] | Sound Pressure Level [NC] | 29.7624
[8 empty] | 34.0268 | 36.0268 | 35.5755 | 36.8941 | 36.0558 | 26.2244
| 40.4097 | 39.9102 | 39.1107 | 45.134 | 12.0206 | 12.0206
Basket A1 40% Setting | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | Basket A2 40% Setting | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz
Sound Power Level (dB) | 29.4097 | 28.9102 | 28.1107 | 34.134 | <5 | <5 | Sound Power Level (dB) | 23.0268 | 25.0268 | 24.5755 | 25.8941 | 25.0558 | 15.2244
Sound Power Level [dB(A)] | 34.8259 | [5 empty] | Sound Power Level [dB(A)] | 30.0967
Sound Pressure Level [dB(A)] | 45.8259 | [5 empty] | Sound Pressure Level [dB(A)] | 41.0967
Sound Pressure Level [NC] | 43.748 | [5 empty] | Sound Pressure Level [NC] | 36.6558
| 48.691 | 50.4087 | 48.7977 | 66.6818 | 9.0103 | 9.0103
Basket A1 20% Setting | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz
Sound Power Level (dB) | 37.691 | 39.4087 | 37.7977 | 55.6818 | <5 | <5
Sound Power Level [dB(A)] | 55.7316
Sound Pressure Level [dB(A)] | 66.7316
Sound Pressure Level [NC] | 65.9422