## BAW-FD
SMARTEMP PRODUCT SELECTION CALCULATOR
Bar Aspiration Wall Diffuser with Removable Core
Project: | <Project Name>
| Inputs | [7 empty] | Detailed Selection | [6 empty] | v 2.0 [11/2025]
| Diffuser Flowrate | 100 | [L/s] | [m3/h] |  |  |  |  | ADPI ≥ | 80% | default ≥ 80%
| VAV (turndown to) | 100 | % 30% to 100% (use 100% for CAV) | [13 empty] | Specific Airflow Rate (heating) | 5 | L/s/m2
[9 empty] | Diffuser Location | Closed Ceiling (≤ 500 mm diffuser to ceiling)
| Maximum Permissible Static Pressure | 15 | Pa default 15 Pa | [6 empty] | Open Ceiling
| ΔT (cooling) | -12 | K 0 K to -15 K (default -12 K)
| Neck Height | 150 | mm 75mm, 100mm, 125mm, 150mm, 200mm
| Diffuser Mounting Height | 2.5 | m 2 m to 5 m
SMARTEMP BAW-FD | [11 empty] | Key: | Suitable | Not Suitable | Warning | Warning
Dimensions* | Width Flangeless Face |  | [mm]
| Width Flanged Face |  | [mm] | 80 | 105 | 130 | 180
| Width of Diffuser Throat |  | [mm] | 50 | 75 | 100 | 150
Dimensions | Active Length |  | [mm] | 200 | 300 | 400 | 500 | 600 | 700 | 800 | 1000
| Neck Height |  | [mm] | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
Airflow | Selected Airflow Rate |  | [L/s] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| Airflow @ Max Static Pressure |  | [L/s] | 95 | 142 | 190 | 237 | 285 | 332 | 379 | 474
| Min Selected Airflow |  | [L/s] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| Min Permissible Airflow @ -12 K |  | [L/s] | 33 | 49 | 65 | 81 | 98 | - | - | -
| Selected Turndown to % |  |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
| Min Permissible % Turndown to |  |  | 33% | 49% | 65% | 81% | 98% | - | - | -
Pressure | Static Pressure @ 100% Airflow |  | [Pa] | 16.7 | 7.4 | 4.2 | 2.7 | 1.9 | 1.4 | 1 | < 1
| Total Pressure @ 100% Airflow |  | [Pa] | 23.5 | 10.4 | 5.9 | 3.8 | 2.6 | 1.9 | 1.5 | < 1
| Max Selected Total Pressure |  | [Pa] | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
Acoustic | Sound Power Level |  | [dB(A)/m] | 45.7 | 37.1 | 31 | 28.7 | 26.5 | 24.6 | 22.7 | 19.5
| Sound Pressure Level * |  | [NC/m] | 30.7 | 22.1 | 16 | 13.7 | 11.5 | < 10 | < 10 | < 10 | * Based on 10 dB(A) room absoprtion
Recommended Distances & Layout | Lmin |  | [m] | 4.1 | 3.4 | 3.2 | 3.0 | 2.8 | 2.7 | 2.7 | 2.6
| Lmax |  | [m] | 12.1 | 13.5 | 12.0 | 11.8 | 11.5 | 11.3 | 11.0 | 10.5
| Bmin |  | [m] | 2.5 | 2.1 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 2.0
| Bmax |  | [m] | 7.4 | 8.2 | 7.3 | 7.5 | 7.6 | 7.8 | 8.0 | 8.4
| Min Diffuser Height |  | [m] | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3
Velocity | Spigot Velocity |  | [m/s] | 5.66 | 3.4 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | - Warning: High spigot velocity. Recommend increasing 'Neck Height'.
| Face Velocity |  | [m/s] | 3.33 | 2.22 | 1.67 | 1.33 | 1.11 | 0.95 | 0.83 | 0.67
Spigot | Spigot Size |  |  | DN150 | DN200 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250
[6 empty] | click here to see product on smartair.asia | [7 empty] | Copyright © 2025 SMARTAIR DIFFUSION
Group Box 53
Group Box 313

## BAW-FD equations (hidden)
Units
Units | 1 | [L/s] | L/s
Units Multiplier | 1 | L/s | L/s
Input Values
Airflow Rate | 100
VAV | 100
Max Static Pressure | 15
dT(cooling) | -12
Room Height | 2.5
Length Ratio | 0
Air Pattern | 1
Specific airflow | 0
neck height | 150
ADPI | 0.8
LRA | #REF!
Ceiling | 1
Room Temperature | #REF! | C
Manual C distance | 0 | m
distance input type | 1
Input Validation
Airflow Rate | 100
VAV | 1
Airflow Rate (TD) | 100
Max Static Pressure | 15
dT(cooling) | 12 | Capped at 6
Room Height | 2.5
Length Ratio | 0
Air Pattern | 1
ADPI | 80%
Local Velocity | 0.29
LRA | #REF!
Ceiling Type | 0 | Closed
Ceiling Type Heating | 1
Ceiling Type Hmin | 1
Cmin Ceiling Factor | 1
Cmax Ceiling Factor | 1
Spigot Selection
Neck Height | 0.15 |  |  |  |  | Selected Spigot Properties
Target Spigot V | 2.5 | Round Spigot |  | Oval Spigot |  | Type | Total Spigot Width | Area | Velocity |  | Distance
| DN | Area | Circumf | OH | Area |  |  |  | Design | Turndown
DN150 | 0.15 | 0.017671 | 0.47124 | 0 | 0.017671 | ROUND | 0.15 | 0.017671 | 5.6588 | 5.6588 | 3.1588
DN200 | 0.2 | 0.031416 | 0.62832 | 0.07854 | 0.029452 | OVAL | 0.22854 | 0.029452 | 3.3953 | 3.3953 | 0.89531
DN250 | 0.25 | 0.049087 | 0.7854 | 0.15708 | 0.041233 | OVAL | 0.30708 | 0.041233 | 2.4252 | 2.4252 | 0.074782
DN300 | 0.3 | 0.070686 | 0.94248 | 0.23562 | 0.053014 | OVAL | 0.38562 | 0.053014 | 1.8863 | 1.8863 | 0.61372
DN350 | 0.35 | 0.096211 | 1.0996 | 0.31416 | 0.064795 | OVAL | 0.46416 | 0.064795 | 1.5433 | 1.5433 | 0.95668
Vmin
95% | 0.43357
90% | 0.4 |  |  |  |  | 0.9 | 40%
80% | 0.3327 |  |  |  |  | 0.7 | 26.55%
70% | 0.2655
80% | 0.3327
Lmin
Throw / Width @ APDI
Face width / Spigot width | 70% | 80% | 90%
1 | 1.5 | 1.7 | 2
3 | 1.2 | 1.3 | 1.5 |  | ADPI | 0.8
m | -0.15 | -0.2 | -0.25 |  | M | -0.2
b | 1.65 | 1.9 | 2.25 |  | B | 1.9
Adjustment Factor | 90% | Standard Data is giving higher coverage than PMW, so adjsutment factor has been added
H | ax | ^b | Target Q''
2.7 | 2886 | 2.152 | 201.0837
4 | 2651 | 2.175 | 179.5252
10.0001 | 2317 | 2.194 | 153.2594
| Ax | ^b
2.5 | 242.1377 | -0.20126 | 201.359 | W/m2
v' for Vmax | 15.1019 | L/s/m2
v' for Vmin | 19.1019 | L/s/m2
v'' + correction factor | 4
Lmax
Throw / Width @ APDI
Face width / Spigot width | 70% | 80% | 90%
1 | 1.5 | 1.7 | 2
3 | 1.2 | 1.3 | 1.5 |  | ADPI | 0.8
m | -0.15 | -0.2 | -0.25 |  | M | -0.2
b | 1.65 | 1.9 | 2.25 |  | B | 1.9
Adjustment Factor | 130% | Standard Data is giving higher coverage than PMW and much higher than stadard bar grille, so adjsutment factor has been added
ADPI | for Vmax | for Vmin |  | Hfactor @ Vmax | Hfactor @ Vmin
95% | 1.91 | 2.54 | L/s/m2 | 5.317 | 4.4309 |  | 95% | 5.73 | 7.62
90% | 1.5 | 2 | L/s/m2 | 6 | 5 |  | 90% | 4.5 | 6
80% | 1 | 1.32 | L/s/m2 | 7.3659 | 6.1383 |  | 80% | 3 | 3.96
70% | 0.7 | 0.94 | L/s/m2 | 8.7318 | 7.2765 |  | 70% | 2.1 | 2.82 | [27 empty] | Q | SWL | P |  | A | B
at Vmax | 1.3 |  | at adpi | 7.3659 |  |  | at Vmax | 3 | [28 empty] | 130 | #REF! | #REF! |  | 15.324 | -2.6401
at Vmin | 1.716 |  |  | 6.1383 |  |  | at Vmin | 3.96 | [28 empty] | 210 | #REF! | #REF!
[37 empty] | 280 | #REF! | #REF!
| V | L/s/m2 |  | The diffuser is not pressure dominant enough to signifigantly reduce the velocity when the face is oversized, therefore it is more appropriate to scale according to spigot velocity.
V'' Min |  | 0.7
at Spigot V = 2.5 m/s | 2.5 | 1.3
at Spigot V = 1.0 m/s | 1 | 1.716
V'' Max |  | 2.5
Hmin
Hmin 1WAY | 2.6056 |  | 0.04282 | 2
ADPI
Hmin | 95% | 2.7056
| 90% | 2.6056
| 85% | 2.5556
| 80% | 2.5056
| 70% | 2.4056
Heating
Height | Slope
2 | 1.0112 | [35 empty] | SWL | #REF!
2.7 | 0.66726
3 | 0.54867
4 | 0.27434
5 | 0.088496
Reference Test
Reference Test (Data is scaled to all sizes)
Reference Flowrate | 90 | L/s |  |  | 120
Reference Length | 0.3 | m |  |  | 0.3
Reference Slots | 10 | slots | (150 high) |  | 10
Reference Total Pressure | 8.45 | Pa |  |  | 10
Reference Sound Power | 40 | db[A]
Vmin | 50% | % |  |  | 30%
Flowrate per slot | 30 | L/s/slot
N Slots for H selection | 10 | Slots
Flowrate per m for H selection | 300 | L/s/m
Coefficients for change in H
Acoustic B | 3.0103 | coef
Length
200 | [6 empty] | 300 | [5 empty] | 400 | [5 empty] | 500 |  |  |  | 600 | [5 empty] | 700 | [5 empty] | 800 | [6 empty] | 1000
L | 0.2 | [5 empty] | L | 0.3 |  |  |  |  | L | 0.4 |  |  |  |  | L | 0.5 |  |  | L | 0.6 |  |  |  |  | L | 0.7 |  |  |  |  | L | 0.8 | [5 empty] | L | 1
data.Flowrate | 60 | L/s |  |  |  |  | data.Flowrate | 90 | L/s |  |  |  | data.Flowrate | 120 | L/s |  |  |  | data.Flowrate | 150 | L/s |  | data.Flowrate | 180 | L/s |  |  |  | data.Flowrate | 210 | L/s |  |  |  | data.Flowrate | 240 | L/s |  |  |  |  | data.Flowrate | 300 | L/s
data.Pressure | 8.45 | Pa |  |  |  |  | data.Pressure | 8.45 | Pa |  |  |  | data.Pressure | 8.45 | Pa |  |  |  | data.Pressure | 8.45 | Pa |  | data.Pressure | 8.45 | Pa |  |  |  | data.Pressure | 8.45 | Pa |  |  |  | data.Pressure | 8.45 | Pa |  |  |  |  | data.Pressure | 8.45 | Pa
Grille Neck Area | 0.03 | m2 |  |  |  |  | Grille Neck Area | 0.045 | m2 |  |  |  | Grille Neck Area | 0.06 | m2 |  |  |  | Grille Neck Area | 0.075 | m2 |  | Grille Neck Area | 0.09 | m2 |  |  |  | Grille Neck Area | 0.105 | m2 |  |  |  | Grille Neck Area | 0.12 | m2 |  |  |  |  | Grille Neck Area | 0.15 | m2
Grille Face Velocity @ Data.Flowrate | 2 | m/s |  |  |  |  | Grille Face Velocity @ Data.Flowrate | 2 | m/s |  |  |  | Grille Face Velocity @ Data.Flowrate | 2 | m/s |  |  |  | Grille Face Velocity @ Data.Flowrate | 2 | m/s |  | Grille Face Velocity @ Data.Flowrate | 2 | m/s |  |  |  | Grille Face Velocity @ Data.Flowrate | 2 | m/s |  |  |  | Grille Face Velocity @ Data.Flowrate | 2 | m/s |  |  |  |  | Grille Face Velocity @ Data.Flowrate | 2 | m/s
data. Static pessure at grille | 6 | Pa |  |  |  |  | Static pressure at grille | 6 |  |  |  |  | Static pressure at grille | 6 |  |  |  |  | Static pressure at grille | 6 |  |  | Static pressure at grille | 6 |  |  |  |  | Static pressure at grille | 6 |  |  |  |  | Static pressure at grille | 6 | [5 empty] | Static pressure at grille | 6
Static Pressure @ Flowrate | 16.6667 | Pa |  |  |  |  | Static Pressure @ Flowrate | 7.4074 | Pa |  |  |  | Static Pressure @ Flowrate | 4.1667 | Pa |  |  |  | Static Pressure @ Flowrate | 2.6667 | Pa |  | Static Pressure @ Flowrate | 1.8519 | Pa |  |  |  | Static Pressure @ Flowrate | 1.3605 | Pa |  |  |  | Static Pressure @ Flowrate | 1.0417 | Pa |  |  |  |  | Static Pressure @ Flowrate | 0.66667 | Pa
Total Pressure @Flowrate | 23.4722 | Pa |  |  |  |  | Total Pressure @Flowrate | 10.4321 | Pa |  |  |  | Total Pressure @Flowrate | 5.8681 | Pa |  |  |  | Total Pressure @Flowrate | 3.7556 | Pa |  | Total Pressure @Flowrate | 2.608 | Pa |  |  |  | Total Pressure @Flowrate | 1.9161 | Pa |  |  |  | Total Pressure @Flowrate | 1.467 | Pa |  |  |  |  | Total Pressure @Flowrate | 0.93889 | Pa
Flowrate @MaxP | 94.8683 | L/s |  |  |  |  | Flowrate @MaxP | 142.3025 | L/s |  |  |  | Flowrate @MaxP | 189.7367 | L/s |  |  |  | Flowrate @MaxP | 237.1708 | L/s |  | Flowrate @MaxP | 284.605 | L/s |  |  |  | Flowrate @MaxP | 332.0392 | L/s |  |  |  | Flowrate @MaxP | 379.4733 | L/s |  |  |  |  | Flowrate @MaxP | 474.3416 | L/s
V_min | 32.5737 | L/s |  |  |  |  | V_min | 48.8605 | L/s |  |  |  | V_min | 65.1474 | L/s |  |  |  | V_min | 81.4342 | L/s |  | V_min | 97.7211 | L/s |  |  |  | V_min | 114.0079 | L/s |  |  |  | V_min | 130.2948 | L/s |  |  |  |  | V_min | 162.8684 | L/s
Min % TD to | 32.57% | % |  |  |  |  | Min % TD to | 48.86% | % |  |  |  | Min % TD to | 65.15% | % |  |  |  | Min % TD to | 81.43% | % |  | Min % TD to | 97.72% | % |  |  |  | Min % TD to | 114% | % |  |  |  | Min % TD to | 130.3% | % |  |  |  |  | Min % TD to | 162.9% | %
SWL - Static Pressure Coefficients | [6 empty] | SWL - Static Pressure Coefficients | [5 empty] | SWL - Static Pressure Coefficients | [5 empty] | SWL - Static Pressure Coefficients |  |  |  | SWL - Static Pressure Coefficients | [5 empty] | SWL - Static Pressure Coefficients | [5 empty] | SWL - Static Pressure Coefficients | [6 empty] | LMC-AD-N1000-4 Sound Power
Effective Neck Length | 0.175 | m |  |  |  |  | Effective Neck Length | 0.26427 | m |  |  |  | Effective Neck Length | 0.35354 | m |  |  |  | Effective Neck Length | 0.40354 | m |  | Effective Neck Length | 0.45354 | m |  |  |  | Effective Neck Length | 0.50354 | m |  |  |  | Effective Neck Length | 0.55354 | m |  |  |  |  | Effective Neck Length | 0.65354 | m
Flowrate L/S/M/4Rows | 228.5714 | L/s/m / 4row |  |  |  |  | Flowrate L/S/M/4Rows | 151.3604 | L/s/m / 4row |  |  |  | Flowrate L/S/M/4Rows | 113.1414 | L/s/m / 4row |  |  |  | Flowrate L/S/M/4Rows | 99.1228 | L/s/m / 4row |  | Flowrate L/S/M/4Rows | 88.1951 | L/s/m / 4row |  |  |  | Flowrate L/S/M/4Rows | 79.4376 | L/s/m / 4row |  |  |  | Flowrate L/S/M/4Rows | 72.2622 | L/s/m / 4row |  |  |  |  | Flowrate L/S/M/4Rows | 61.2051 | L/s/m / 4row
LMC-AD-N100-4 Data Flowrate | 149 | [5 empty] | LMC-AD-N100-4 Data Flowrate | 149 |  |  |  |  | LMC-AD-N100-4 Data Flowrate | 149 |  |  |  |  | LMC-AD-N100-4 Data Flowrate | 149 |  |  | LMC-AD-N100-4 Data Flowrate | 149 |  |  |  |  | LMC-AD-N100-4 Data Flowrate | 149 |  |  |  |  | LMC-AD-N100-4 Data Flowrate | 149 | [5 empty] | LMC-AD-N100-4 Data Flowrate | 149
LMC-AD-N100-4 Data Static | 32.2785 | [5 empty] | LMC-AD-N100-4 Data Static | 32.2785 |  |  |  |  | LMC-AD-N100-4 Data Static | 32.2785 |  |  |  |  | LMC-AD-N100-4 Data Static | 32.2785 |  |  | LMC-AD-N100-4 Data Static | 32.2785 |  |  |  |  | LMC-AD-N100-4 Data Static | 32.2785 |  |  |  |  | LMC-AD-N100-4 Data Static | 32.2785 | [5 empty] | LMC-AD-N100-4 Data Static | 32.2785
LMC-AD-N100-4 Static | 75.9599 | [5 empty] | LMC-AD-N100-4 Static | 33.3093 |  |  |  |  | LMC-AD-N100-4 Static | 18.6116 |  |  |  |  | LMC-AD-N100-4 Static | 14.2852 |  |  | LMC-AD-N100-4 Static | 11.3091 |  |  |  |  | LMC-AD-N100-4 Static | 9.1747 |  |  |  |  | LMC-AD-N100-4 Static | 7.5921 | [5 empty] | LMC-AD-N100-4 Static | 5.4465
A | 12.575 | [5 empty] | A | 12.575 |  |  |  |  | A | 12.575 |  |  |  |  | A | 12.575 |  |  | A | 12.575 |  |  |  |  | A | 12.575 |  |  |  |  | A | 12.575 | [5 empty] | A | 12.575
B | -5.7516 | [5 empty] | B | -5.7516 |  |  |  |  | B | -5.7516 |  |  |  |  | B | -5.7516 |  |  | B | -5.7516 |  |  |  |  | B | -5.7516 |  |  |  |  | B | -5.7516 | [5 empty] | B | -5.7516
SWL LMC-AD-N1000-4 | 48.7007 | [5 empty] | SWL LMC-AD-N1000-4 | 38.3343 |  |  |  |  | SWL LMC-AD-N1000-4 | 31.015 |  |  |  |  | SWL LMC-AD-N1000-4 | 27.6882 |  |  | SWL LMC-AD-N1000-4 | 24.7505 |  |  |  |  | SWL LMC-AD-N1000-4 | 22.1203 |  |  |  |  | SWL LMC-AD-N1000-4 | 19.7393 | [5 empty] | SWL LMC-AD-N1000-4 | 15.5627
Row Factor | 2.5 | [5 empty] | Row Factor | 2.5 |  |  |  |  | Row Factor | 2.5 |  |  |  |  | Row Factor | 2.5 |  |  | Row Factor | 2.5 |  |  |  |  | Row Factor | 2.5 |  |  |  |  | Row Factor | 2.5 | [5 empty] | Row Factor | 2.5
Length Factor | 0.2 | [5 empty] | Length Factor | 0.3 |  |  |  |  | Length Factor | 0.4 |  |  |  |  | Length Factor | 0.5 |  |  | Length Factor | 0.6 |  |  |  |  | Length Factor | 0.7 |  |  |  |  | Length Factor | 0.8 | [5 empty] | Length Factor | 1
SWL LMC-AD-N200-N____ | 45.6904 | [5 empty] | SWL LMC-AD-N300-N____ | 37.0849 |  |  |  |  | SWL LMC-AD-N400-N____ | 31.015 |  |  |  |  | SWL LMC-AD-N500-N____ | 28.6573 |  |  | SWL LMC-AD-N600-N____ | 26.5114 |  |  |  |  | SWL LMC-AD-N700-R____ | 24.5507 |  |  |  |  | SWL LMC-AD-N800-R____ | 22.7496 | [5 empty] | SWL LMC-AD-N1000-R____ | 19.5421 | Scale SWL to Neck length and Rows
Factor | 1 | [5 empty] | Factor | 1 |  |  |  |  | Factor | 1 |  |  |  |  | Factor | 1 |  |  | Factor | 1 |  |  |  |  | Factor | 1 |  |  |  |  | Factor | 1 | [5 empty] | Factor | 1
SWL | 45.6904 | [5 empty] | SWL | 37.0849 |  |  |  |  | SWL | 31.015 |  |  |  |  | SWL | 28.6573 |  |  | SWL | 26.5114 |  |  |  |  | SWL | 24.5507 |  |  |  |  | SWL | 22.7496 | [5 empty] | SWL | 19.5421
SPL | 30.6904 | [5 empty] | SPL | 22.0849 |  |  |  |  | SPL | 16.015 |  |  |  |  | SPL | 13.6573 |  |  | SPL | 11.5114 |  |  |  |  | SPL | 9.5507 |  |  |  |  | SPL | 7.7496 | [5 empty] | SPL | 4.5421
Spigot Area [m2]
| Distance | Fits? | Spigot |  |  |  |  | Distance | Fits? | Spigot |  |  |  | Distance | Fits? | Spigot |  |  |  | Distance | Fits? | Spigot |  | Distance | Fits? | Spigot |  |  |  | Distance | Fits? | Spigot |  |  |  | Distance | Fits? | Spigot |  |  |  |  | Distance | Fits? | Spigot
| 3.1588 | 1 | DN150 |  |  |  |  | 3.1588 | 1 | DN150 |  |  |  | 3.1588 | 1 | DN150 |  |  |  | 3.1588 | 1 | DN150 |  | 3.1588 | 1 | DN150 |  |  |  | 3.1588 | 1 | DN150 |  |  |  | 3.1588 | 1 | DN150 |  |  |  |  | 3.1588 | 1 | DN150
| 10000 | 0 | DN200 |  |  |  |  | 0.89531 | 1 | DN200 |  |  |  | 0.89531 | 1 | DN200 |  |  |  | 0.89531 | 1 | DN200 |  | 0.89531 | 1 | DN200 |  |  |  | 0.89531 | 1 | DN200 |  |  |  | 0.89531 | 1 | DN200 |  |  |  |  | 0.89531 | 1 | DN200
| 10000 | 0 | DN250 |  |  |  |  | 10000 | 0 | DN250 |  |  |  | 0.074782 | 1 | DN250 |  |  |  | 0.074782 | 1 | DN250 |  | 0.074782 | 1 | DN250 |  |  |  | 0.074782 | 1 | DN250 |  |  |  | 0.074782 | 1 | DN250 |  |  |  |  | 0.074782 | 1 | DN250
| 10000 | 0 | DN300 |  |  |  |  | 10000 | 0 | DN300 |  |  |  | 0.61372 | 1 | DN300 |  |  |  | 0.61372 | 1 | DN300 |  | 0.61372 | 1 | DN300 |  |  |  | 0.61372 | 1 | DN300 |  |  |  | 0.61372 | 1 | DN300 |  |  |  |  | 0.61372 | 1 | DN300
| 10000 | 0 | DN350 |  |  |  |  | 10000 | 0 | DN350 |  |  |  | 10000 | 0 | DN350 |  |  |  | 0.95668 | 1 | DN350 |  | 0.95668 | 1 | DN350 |  |  |  | 0.95668 | 1 | DN350 |  |  |  | 0.95668 | 1 | DN350 |  |  |  |  | 0.95668 | 1 | DN350
Spigot | DN150 | [5 empty] | Spigot | DN200 |  |  |  |  | Spigot | DN250 |  |  |  |  | Spigot | DN250 |  |  | Spigot | DN250 |  |  |  |  | Spigot | DN250 |  |  |  |  | Spigot | DN250 | [5 empty] | Spigot | DN250
Spigot Velocity @ Design | 5.6588 | [5 empty] | Spigot Velocity @ Design | 3.3953 |  |  |  |  | Spigot Velocity @ Design | 2.4252 |  |  |  |  | Spigot Velocity @ Design | 2.4252 |  |  | Spigot Velocity @ Design | 2.4252 |  |  |  |  | Spigot Velocity @ Design | 2.4252 |  |  |  |  | Spigot Velocity @ Design | 2.4252 | [5 empty] | Spigot Velocity @ Design | 2.4252
Spigot Velocity @ Turndown | 5.6588 | [5 empty] | Spigot Velocity @ Turndown | 3.3953 |  |  |  |  | Spigot Velocity @ Turndown | 2.4252 |  |  |  |  | Spigot Velocity @ Turndown | 2.4252 |  |  | Spigot Velocity @ Turndown | 2.4252 |  |  |  |  | Spigot Velocity @ Turndown | 2.4252 |  |  |  |  | Spigot Velocity @ Turndown | 2.4252 | [5 empty] | Spigot Velocity @ Turndown | 2.4252
Face Velocity | 3.3333 | [5 empty] | Face Velocity | 2.2222 |  |  |  |  | Face Velocity | 1.6667 |  |  |  |  | Face Velocity | 1.3333 |  |  | Face Velocity | 1.1111 |  |  |  |  | Face Velocity | 0.95238 |  |  |  |  | Face Velocity | 0.83333 | [5 empty] | Face Velocity | 0.66667
Spigot Width | 0.15 | [5 empty] | Spigot Width | 0.22854 |  |  |  |  | Spigot Width | 0.30708 |  |  |  |  | Spigot Width | 0.30708 |  |  | Spigot Width | 0.30708 |  |  |  |  | Spigot Width | 0.30708 |  |  |  |  | Spigot Width | 0.30708 | [5 empty] | Spigot Width | 0.30708
Box Width | 0.2 | [5 empty] | Box Width | 0.3 |  |  |  |  | Box Width | 0.4 |  |  |  |  | Box Width | 0.5 |  |  | Box Width | 0.6 |  |  |  |  | Box Width | 0.7 |  |  |  |  | Box Width | 0.8 | [5 empty] | Box Width | 1
Face width / Spigot width | 1.3333 | [5 empty] | Face width / Spigot width | 1.3127 |  |  |  |  | Face width / Spigot width | 1.3026 |  |  |  |  | Face width / Spigot width | 1.6282 |  |  | Face width / Spigot width | 1.9539 |  |  |  |  | Face width / Spigot width | 2.2795 |  |  |  |  | Face width / Spigot width | 2.6052 | [5 empty] | Face width / Spigot width | 3.2565
Min Diffuser Height (m) | 2.3 |  | Do not exceed the max spec airflow |  |  |  | Min Diffuser Height (m) | 2.3 |  |  |  |  | Min Diffuser Height (m) | 2.3 |  |  |  |  | Min Diffuser Height (m) | 2.3 |  |  | Min Diffuser Height (m) | 2.3 |  |  |  |  | Min Diffuser Height (m) | 2.3 |  |  |  |  | Min Diffuser Height (m) | 2.3 | [5 empty] | Min Diffuser Height (m) | 2.3
|  |  |  | Flowrate | 100
Distance Selection | 50% |  |  | L/s/m2 | Area |  | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection |  |  |  | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection | [6 empty] | Distance Selection
Vmax | 60 |  | Design | 15.1019 | 6.6217 |  | Vmax | 90 |  |  |  |  | Vmax | 120 |  |  |  |  | Vmax | 150 |  |  | Vmax | 180 |  |  |  |  | Vmax | 210 |  |  |  |  | Vmax | 240 | [5 empty] | Vmax | 300
Vmin | 30 |  | Min | 19.1019 | 5.2351 |  | Vmin | 45 |  |  |  |  | Vmin | 60 |  |  |  |  | Vmin | 75 |  |  | Vmin | 90 |  |  |  |  | Vmin | 105 |  |  |  |  | Vmin | 120 | [5 empty] | Vmin | 150
Lmin & Bmin | [6 empty] | Lmin & Bmin | [5 empty] | Lmin & Bmin | [5 empty] | Lmin & Bmin |  |  |  | Lmin & Bmin | [5 empty] | Lmin & Bmin | [5 empty] | Lmin & Bmin | [6 empty] | Lmin & Bmin
v"at V (L/s/m^2) | 9.7686 | L/s/m2 |  |  |  |  | at V (L/s/m^2) | 14.213 |  |  |  |  | at V (L/s/m^2) | 16.4353 |  |  |  |  | at V (L/s/m^2) | 17.7686 |  |  | at V (L/s/m^2) | 18.6575 |  |  |  |  | at V (L/s/m^2) | 19.2924 |  |  |  |  | at V (L/s/m^2) | 19.7686 | [5 empty] | at V (L/s/m^2) | 20.4353
V'' Max | 9.7686 | L/s/m2 | Do not exceed Vmin spec airflow |  |  |  | V'' Max | 14.213 | L/s/m2 | Do not exceed Vmin spec airflow |  |  | V'' Max | 16.4353 | L/s/m2 | Do not exceed Vmin spec airflow |  |  | V'' Max | 17.7686 | L/s/m2 | Do not exceed Vmin spec airflow | V'' Max | 18.6575 | L/s/m2 | Do not exceed Vmin spec airflow |  |  | V'' Max | 19.1019 | L/s/m2 | Do not exceed Vmin spec airflow |  |  | V'' Max | 19.1019 | L/s/m2 | Do not exceed Vmin spec airflow |  |  |  | V'' Max | 19.1019 | L/s/m2 | Do not exceed Vmin spec airflow
Area | 10.2369 | m2 |  |  |  |  | Area | 7.0358 |  | * Cmin Area | 2.6525 |  | Area | 6.0845 |  |  |  |  | Area | 5.6279 |  |  | Area | 5.3598 |  |  |  |  | Area | 5.2351 |  |  |  |  | Area | 5.2351 | [5 empty] | Area | 5.2351
Lmin Coverage Aspect | 1.6333 | Lmin / Bmin |  |  |  |  | Lmin Coverage Aspect | 1.6375 |  |  |  |  | Lmin Coverage Aspect | 1.6395 |  |  |  |  | Lmin Coverage Aspect | 1.5744 |  |  | Lmin Coverage Aspect | 1.5092 |  |  |  |  | Lmin Coverage Aspect | 1.4441 |  |  |  |  | Lmin Coverage Aspect | 1.379 | [5 empty] | Lmin Coverage Aspect | 1.2487
Lmin | 4.089 | [5 empty] | Lmin | 3.3942 |  |  |  |  | Lmin | 3.1584 |  |  |  |  | Lmin | 2.9766 |  |  | Lmin | 2.8441 |  |  |  |  | Lmin | 2.7495 |  |  |  |  | Lmin | 2.6868 | [5 empty] | Lmin | 2.5568
Bmin | 2.5035 | [5 empty] | Bmin | 2.0729 |  |  |  |  | Bmin | 1.9265 |  |  |  |  | Bmin | 1.8907 |  |  | Bmin | 1.8845 |  |  |  |  | Bmin | 1.904 |  |  |  |  | Bmin | 1.9484 | [5 empty] | Bmin | 2.0475
|  |  | Flowrate | 100
|  |  | Design | 1.3 | L/s/m2
|  |  | Min | 1.716 | L/s/m2
Lmax & Bmax | [6 empty] | Lmax & Bmax | [5 empty] | Lmax & Bmax | [5 empty] | Lmax & Bmax |  |  |  | Lmax & Bmax | [5 empty] | Lmax & Bmax | [5 empty] | Lmax & Bmax | [6 empty] | Lmax & Bmax
Spigot Velocity @ Turndown | 5.6588 | [5 empty] | Spigot Velocity @ Turndown | 3.3953 |  |  |  |  | Spigot Velocity @ Turndown | 2.4252 |  |  |  |  | Spigot Velocity @ Turndown | 2.4252 |  |  | Spigot Velocity @ Turndown | 2.4252 |  |  |  |  | Spigot Velocity @ Turndown | 2.4252 |  |  |  |  | Spigot Velocity @ Turndown | 2.4252 | [5 empty] | Spigot Velocity @ Turndown | 2.4252
v'' @ Vmin | 0.42395 | l/s/m2 |  |  |  |  | v'' @ Vmin | 1.0517 | l/s/m2 |  |  |  | v'' @ Vmin | 1.3207 | l/s/m2 |  |  |  | v'' @ Vmin | 1.3207 | l/s/m2 |  | v'' @ Vmin | 1.3207 | l/s/m2 |  |  |  | v'' @ Vmin | 1.3207 | l/s/m2 |  |  |  | v'' @ Vmin | 1.3207 | l/s/m2 |  |  |  |  | v'' @ Vmin | 1.3207 | l/s/m2
Vmin < V'' < Vmax | 1.3 | L/s/m2 |  |  |  |  | Vmin < V'' < Vmax | 1.0517 | L/s/m2 |  |  |  | Vmin < V'' < Vmax | 1.3207 | L/s/m2 |  |  |  | Vmin < V'' < Vmax | 1.3207 | L/s/m2 |  | Vmin < V'' < Vmax | 1.3207 | L/s/m2 |  |  |  | Vmin < V'' < Vmax | 1.3207 | L/s/m2 |  |  |  | Vmin < V'' < Vmax | 1.3207 | L/s/m2 |  |  |  |  | Vmin < V'' < Vmax | 1.3207 | L/s/m2
Area | 76.9231 | m2 |  |  |  |  | Area | 95.084 | m2 |  |  |  | Area | 75.7152 | m2 |  |  |  | Area | 75.7152 | m2 |  | Area | 75.7152 | m2 |  |  |  | Area | 75.7152 | m2 |  |  |  | Area | 75.7152 | m2 |  |  |  |  | Area | 75.7152 | m2
Lmax Coverage Aspect | 1.6333 | Lmax/Bmax |  |  |  |  | Lmax Coverage Aspect | 1.6375 |  |  |  |  | Lmax Coverage Aspect | 1.6395 |  |  |  |  | Lmax Coverage Aspect | 1.5744 |  |  | Lmax Coverage Aspect | 1.5092 |  |  |  |  | Lmax Coverage Aspect | 1.4441 |  |  |  |  | Lmax Coverage Aspect | 1.379 | [5 empty] | Lmax Coverage Aspect | 1.2487
Lmax | 11.209 | m |  |  |  |  | Lmax | 12.4778 | m |  |  |  | Lmax | 11.1415 | m |  |  |  | Lmax | 10.918 | m |  | Lmax | 10.6898 | m |  |  |  | Lmax | 10.4566 | m |  |  |  | Lmax | 10.218 | m |  |  |  |  | Lmax | 9.7235 | m
Lmax (room height adjusted) | 12.1057 | m |  |  |  |  | Lmax (room height adjusted) | 13.4761 | m |  |  |  | Lmax (room height adjusted) | 12.0328 | m |  |  |  | Lmax (room height adjusted) | 11.7914 | m |  | Lmax (room height adjusted) | 11.5449 | m |  |  |  | Lmax (room height adjusted) | 11.2931 | m |  |  |  | Lmax (room height adjusted) | 11.0355 | m |  |  |  |  | Lmax (room height adjusted) | 10.5013 | m
h factor @ V | 9.0028 | [5 empty] | h factor @ V | 7.6387 |  |  |  |  | h factor @ V | 6.9567 |  |  |  |  | h factor @ V | 6.5475 |  |  | h factor @ V | 6.2747 |  |  |  |  | h factor @ V | 6.0798 |  |  |  |  | h factor @ V | 5.9337 | [5 empty] | h factor @ V | 5.7291
Lmax room height | 22.507 | m |  |  |  |  | Lmax room height | 19.0968 | m |  |  |  | Lmax room height | 17.3918 | m |  |  |  | Lmax room height | 16.3687 | m |  | Lmax room height | 15.6867 | m |  |  |  | Lmax room height | 15.1995 | m |  |  |  | Lmax room height | 14.8342 | m |  |  |  |  | Lmax room height | 14.3226 | m
Lmax Min of above | 12.1057 | m |  |  |  |  | Lmax Min of above | 13.4761 | m |  |  |  | Lmax Min of above | 12.0328 | m |  |  |  | Lmax Min of above | 11.7914 | m |  | Lmax Min of above | 11.5449 | m |  |  |  | Lmax Min of above | 11.2931 | m |  |  |  | Lmax Min of above | 11.0355 | m |  |  |  |  | Lmax Min of above | 10.5013 | m
Lmax DT & ceiling factor Adusted | 12.1057 | m |  |  |  |  | Lmax DT & ceiling factor Adusted | 13.4761 | m |  |  |  | Lmax DT & ceiling factor Adusted | 12.0328 | m |  |  |  | Lmax DT & ceiling factor Adusted | 11.7914 | m |  | Lmax DT & ceiling factor Adusted | 11.5449 | m |  |  |  | Lmax DT & ceiling factor Adusted | 11.2931 | m |  |  |  | Lmax DT & ceiling factor Adusted | 11.0355 | m |  |  |  |  | Lmax DT & ceiling factor Adusted | 10.5013 | m
Bmax | 7.4116 | m |  |  |  |  | Bmax | 8.2298 | m |  |  |  | Bmax | 7.3394 | m |  |  |  | Bmax | 7.4897 | m |  | Bmax | 7.6496 | m |  |  |  | Bmax | 7.8202 | m |  |  |  | Bmax | 8.0027 | m |  |  |  |  | Bmax | 8.4098 | m
Heating | [6 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating |  |  |  | Heating | [5 empty] | Heating | [5 empty] | Heating | [6 empty] | Heating
V Average | 2.4911 | L/s/m2 |  |  |  |  | V Average | 2.3014 | L/s/m3 |  |  |  | V Average | 2.8417 | L/s/m4 |  |  |  | V Average | 2.8875 | L/s/m5 |  | V Average | 2.9157 | L/s/m6 |  |  |  | V Average | 2.9293 | L/s/m7 |  |  |  | V Average | 2.9293 | L/s/m8 |  |  |  |  | V Average | 2.9293 | L/s/m9
V'' adjusted for heating | 2.4911 | L/s/m2 |  |  |  |  | V'' adjusted for heating | 2.3014 | L/s/m2 |  |  |  | V'' adjusted for heating | 2.8417 | L/s/m2 |  |  |  | V'' adjusted for heating | 2.8875 | L/s/m2 |  | V'' adjusted for heating | 2.9157 | L/s/m2 |  |  |  | V'' adjusted for heating | 2.9293 | L/s/m2 |  |  |  | V'' adjusted for heating | 2.9293 | L/s/m2 |  |  |  |  | V'' adjusted for heating | 2.9293 | L/s/m2
heatingX | 7.655 |  | -0.0001794 | 0.1058 | -1.131 |  | heatingX | 0 |  |  |  |  | heatingX | 4.954 |  | -0.0001152 | 0.08117 | -2.011 | heatingX | 0 |  |  | heatingX | 6.757 |  | -0.0001424 | 0.0949 | -1.309 | heatingX | 6.757 |  | -0.0001424 | 0.0949 | -1.309 | heatingX | 6.757 |  | -0.0001424 | 0.0949 | -1.309 |  | heatingX | 6.757 |  | -0.0001424 | 0.0949 | -1.309
heatingSlope | 0.76554 | [5 empty] | heatingSlope | 0.76554 |  |  |  |  | heatingSlope | 0.76554 |  |  |  |  | heatingSlope | 0.76554 |  |  | heatingSlope | 0.76554 |  |  |  |  | heatingSlope | 0.76554 |  |  |  |  | heatingSlope | 0.76554 | [5 empty] | heatingSlope | 0.76554
heatingY | 5.8602 | [5 empty] | heatingY | 0 |  |  |  |  | heatingY | 3.7925 |  |  |  |  | heatingY | 0 |  |  | heatingY | 5.1727 |  |  |  |  | heatingY | 5.1727 |  |  |  |  | heatingY | 5.1727 | [5 empty] | heatingY | 5.1727
heating_dT(10K) | 13.0213 |  |  | 2.222 |  |  | heating_dT(10K) | 0 |  |  |  |  | heating_dT(10K) | 8.4269 |  |  | 2.222 |  | heating_dT(10K) | 0 |  |  | heating_dT(10K) | 11.4938 |  |  | 2.222 |  | heating_dT(10K) | 11.4938 |  |  | 2.222 |  | heating_dT(10K) | 11.4938 |  |  | 2.222 |  |  | heating_dT(10K) | 11.4938 |  |  | 2.222
(old) heating @ dT | #REF! |  | -0.00451 | 0.09517 | 0.4993 |  | heating @ dT | #REF! |  |  |  |  | heating @ dT | #REF! |  | -0.00451 | 0.09517 | 0.4993 | heating @ dT | #REF! |  |  | heating @ dT | #REF! |  | -0.00451 | 0.09517 | 0.4993 | heating @ dT | #REF! |  | -0.00451 | 0.09517 | 0.4993 | heating @ dT | #REF! |  | -0.00451 | 0.09517 | 0.4993 |  | heating @ dT | #REF! |  | -0.00451 | 0.09517 | 0.4993
heating dT (perimeter) | #REF! | [5 empty] | heating dT (perimeter) | #REF! |  |  |  |  | heating dT (perimeter) | #REF! |  |  |  |  | heating dT (perimeter) | #REF! |  |  | heating dT (perimeter) | #REF! |  |  |  |  | heating dT (perimeter) | #REF! |  |  |  |  | heating dT (perimeter) | #REF! | [5 empty] | heating dT (perimeter) | #REF!
heating dT (centre) | #REF! | [5 empty] | heating dT (centre) | #REF! |  |  |  |  | heating dT (centre) | #REF! |  |  |  |  | heating dT (centre) | #REF! |  |  | heating dT (centre) | #REF! |  |  |  |  | heating dT (centre) | #REF! |  |  |  |  | heating dT (centre) | #REF! | [5 empty] | heating dT (centre) | #REF!
Pre-Results
Length | 200 | 300 | 400 | 500 | 600 | 700 | 800 | 1000
Max Airflow (L/s/m) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Max Recommended Airflow (L/s) | 94.8683 | 142.3025 | 189.7367 | 237.1708 | 284.605 | 332.0392 | 379.4733 | 474.3416
Min Airflow (L/s/m) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Min Permissible Airflow | 32.5737 | 48.8605 | 65.1474 | 81.4342 | 97.7211 | 114.0079 | 130.2948 | 162.8684
Min % Turndown to | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Min Permissible % Turndown to | 32.57% | 48.86% | 65.15% | 81.43% | 97.72% | 114% | 130.3% | 162.9%
Max Static Pressure (Pa) | 16.6667 | 7.4074 | 4.1667 | 2.6667 | 1.8519 | 1.3605 | 1.0417 | 0.66667
Max Total Pressure (Pa) | 23.4722 | 10.4321 | 5.8681 | 3.7556 | 2.608 | 1.9161 | 1.467 | 0.93889
Max Permissible Pressure (Pa) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
Sound Power Level (dBA) | 45.6904 | 37.0849 | 31.015 | 28.6573 | 26.5114 | 24.5507 | 22.7496 | 19.5421
Sound Pressure Level (NC) | 30.6904 | 22.0849 | 16.015 | 13.6573 | 11.5114 | 9.5507 | 7.7496 | 4.5421
Max Permissible ΔT (centre) (K) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Max Permissible ΔT (heating) (K) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Spigot Width | 0.15 | 0.22854 | 0.30708 | 0.30708 | 0.30708 | 0.30708 | 0.30708 | 0.30708
Spigot / Face Ratio | 1.3333 | 1.3127 | 1.3026 | 1.6282 | 1.9539 | 2.2795 | 2.6052 | 3.2565
Lmin | 4.089 | 3.3942 | 3.1584 | 2.9766 | 2.8441 | 2.7495 | 2.6868 | 2.5568
Lmax | 12.1057 | 13.4761 | 12.0328 | 11.7914 | 11.5449 | 11.2931 | 11.0355 | 10.5013
Bmin | 2.5035 | 2.0729 | 1.9265 | 1.8907 | 1.8845 | 1.904 | 1.9484 | 2.0475
Bmax | 7.4116 | 8.2298 | 7.3394 | 7.4897 | 7.6496 | 7.8202 | 8.0027 | 8.4098
Min Coverage | 10.2369 | 7.0358 | 6.0845 | 5.6279 | 5.3598 | 5.2351 | 5.2351 | 5.2351
Max Coverage | 89.7231 | 110.9059 | 88.3142 | 88.3142 | 88.3142 | 88.3142 | 88.3142 | 88.3142
Min Diffuser Height (m) | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3
Spigot Velocity | 5.6588 | 3.3953 | 2.4252 | 2.4252 | 2.4252 | 2.4252 | 2.4252 | 2.4252
Face Velocity | 3.3333 | 2.2222 | 1.6667 | 1.3333 | 1.1111 | 0.95238 | 0.83333 | 0.66667
Nominal Spigot Size | DN150 | DN200 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250
Velocity
Results
Length | 200 | 300 | 400 | 500 | 600 | 700 | 800 | 1000
Selected Airflow [L/s] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Airflow @ Max Static Pressure[L/s] | 95 | 142 | 190 | 237 | 285 | 332 | 379 | 474
Min Selected Airflow [L/s] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Min Permissible Airflow @ -12 K | 33 | 49 | 65 | 81 | 98 | 114 | 130 | 163
Min % Turndown to | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Min Permissible % Turndown to | 33% | 49% | 65% | 81% | 98% | 114% | 130% | 163%
Max Static Pressure (Pa) | 16.7 | 7.4 | 4.2 | 2.7 | 1.9 | 1.4 | 1 | < 1
Max Total Pressure (Pa) | 23.5 | 10.4 | 5.9 | 3.8 | 2.6 | 1.9 | 1.5 | < 1
Max Permissible Pressure (Pa) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
Sound Power Level (dBA) | 45.7 | 37.1 | 31 | 28.7 | 26.5 | 24.6 | 22.7 | 19.5
Sound Pressure Level (NC) | 30.7 | 22.1 | 16 | 13.7 | 11.5 | < 10 | < 10 | < 10
Max Permissible ΔT (centre) (K) | ≈ 0.0 | ≈ 0.0 | ≈ 0.0 | ≈ 0.0 | ≈ 0.0 | ≈ 0.0 | ≈ 0.0 | ≈ 0.0
Max Permissible ΔT (heating) (K) | ≈ 0.0 | ≈ 0.0 | ≈ 0.0 | ≈ 0.0 | ≈ 0.0 | ≈ 0.0 | ≈ 0.0 | ≈ 0.0
Lmin | 4.1 | 3.4 | 3.2 | 3 | 2.8 | 2.7 | 2.7 | 2.6
Lmax | 12.1 | 13.5 | 12 | 11.8 | 11.5 | 11.3 | 11 | 10.5
Bmin | 2.5 | 2.1 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 2
Bmax | 7.4 | 8.2 | 7.3 | 7.5 | 7.6 | 7.8 | 8 | 8.4
Min Coverage | 10.2 | 7 | 6.1 | 5.6 | 5.4 | 5.2 | 5.2 | 5.2
Max Coverage | 89.7 | 110.9 | 88.3 | 88.3 | 88.3 | 88.3 | 88.3 | 88.3
Min Diffuser Height (m) | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3
Spigot Velocity | 5.66 | 3.4 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43
Face Velocity | 3.33 | 2.22 | 1.67 | 1.33 | 1.11 | 0.95 | 0.83 | 0.67
Nominal Spigot Size | DN150 | DN200 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250
Results
Length | 200 | 300 | 400 | 500 | 600 | 700 | 800 | 1000
Selected Airflow [L/s] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Airflow @ Max Static Pressure[L/s] | 95 | 142 | 190 | 237 | 285 | 332 | 379 | 474
Min Selected Airflow [L/s] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  |  |  | ¹
Min Permissible Airflow @ -12 K | 33 | 49 | 65 | 81 | 98 | - | - | -
Min % Turndown to | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Min Permissible % Turndown to | 0.33 | 0.49 | 0.65 | 0.81 | 0.98 | - | - | -
Max Static Pressure (Pa) | 16.7 | 7.4 | 4.2 | 2.7 | 1.9 | 1.4 | 1 | < 1
Max Total Pressure (Pa) | 23.5 | 10.4 | 5.9 | 3.8 | 2.6 | 1.9 | 1.5 | < 1
Max Permissible Pressure (Pa) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
Sound Power Level (dBA) | 45.7 | 37.1 | 31 | 28.7 | 26.5 | 24.6 | 22.7 | 19.5
Sound Pressure Level (NC) | 30.7 | 22.1 | 16 | 13.7 | 11.5 | < 10 | < 10 | < 10
Max Permissible ΔT (centre) (K) | ≈ 0.0 | ≈ 0.0 | ≈ 0.0 | ≈ 0.0 | ≈ 0.0 | ≈ 0.0 | ≈ 0.0 | ≈ 0.0
Max Permissible ΔT (heating) (K) | ≈ 0.0 | ≈ 0.0 | ≈ 0.0 | ≈ 0.0 | ≈ 0.0 | ≈ 0.0 | ≈ 0.0 | ≈ 0.0
Lmin | 4.1 | 3.4 | 3.2 | 3.0 | 2.8 | 2.7 | 2.7 | 2.6
Lmax | 12.1 | 13.5 | 12.0 | 11.8 | 11.5 | 11.3 | 11.0 | 10.5
Bmin | 2.5 | 2.1 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 2.0
Bmax | 7.4 | 8.2 | 7.3 | 7.5 | 7.6 | 7.8 | 8.0 | 8.4
Min Coverage | 10.2 | 7 | 6.1 | 5.6 | 5.4 | 5.2 | 5.2 | 5.2
Max Coverage | 89.7 | 110.9 | 88.3 | 88.3 | 88.3 | 88.3 | 88.3 | 88.3
Min Diffuser Height (m) | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3
Spigot Velocity | 5.66 | 3.4 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43
Face Velocity | 3.33 | 2.22 | 1.67 | 1.33 | 1.11 | 0.95 | 0.83 | 0.67
Nominal Spigot Size | DN150 | DN200 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250
Lmin/Lmax = '-' | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
Lmin/Lmax Note
Shading
low pressure | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE = SHADE
high pressure | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE
pressure shade | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE
Acoustic Shade | A | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
max flow | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
min flow | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE
Lmin>Lmax | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
Show Lmin Note | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
Spigot Velocity <= 4 | R | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | - Warning: High spigot velocity. Recommend increasing 'Neck Height'.
Spigot Velocity not suitable | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
Shade | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE
Coverage Aspect = M*(FACE/SPIGOT) + b
Coverage Aspect = M*(FACE/SPIGOT) + b

## data (hidden)
ADPI
95% | 0.2
90% | 0.25
80% | 0.29
70% | 0.33
Slots
| 1 | 1
Length
| Selection | Code | Type | Description
| 1 | N1200 | Neck | 1200 mm neck length
| 2 | N1500 | Neck | 1500 mm neck length
| 3 | <length> | Custom | Custom length
Length | 1 | N1200 | Neck | 1200 mm neck length
Neck Height
75
100
125
150
200
Barrel Setting
| Selection | Display | Code | Name
| 1 | 10.2 | 110.2 | recommended (10.2)
| 2 | Custom Horizontal/Vertical | <direction> | Custom discharge direction
airpatterletter | 1 | 10.2 | 110.2 | recommended (10.2)
Side Profile |  | Code | Description
| 1 | SF | with side flanges
| 2 | SN | flangeless side profile
| 1 | SF | with side flanges
Selection
Diffuser Ends
|  | Code | Description
| 1 | E2 | with two end flanges
| 2 | E1 | with one end flange + one pair of joining strips
| 3 | J | include one pair of joining strips
| 4 | E0 | without end flanges
Selection | 1 | E2 | with two end flanges
Fixing |  | Code | Description
| 1 | F0 | fixing by others; without accessories
| 2 | EX | expansion bracket fixing
Selection | 1 | F0 | fixing by others; without accessories
Colour | RAL9003 | 1 | #REF!
Barrel | B | 1
connection box
| 1 | K0 | no connection box
| 2 | K | uninsulated connection box
| 3 | KI | internally insulated connection box
Selection | 1 | K0 | no connection box
0
| 1 | t | clipped to diffuser throat
| 2 | n | screwed to diffuser throat
Selection | 1
0
Selection |  | K0 | no connection box
Naming
| nominal length | nslots | airpattern letter | profile type | diffuserends | fixing | profile colour | barrelcolour | Box
SMARTEMP LMW-AD- | N1200- | 1- | 110.2- | SF- | E2- | F0- | RAL9003- | B- | K0
SMARTEMP LMW-AD-N1200-1-110.2-SF-E2-F0-RAL9003-B-K0
Bespoke dimensions
Summary
Length | Neck 1200 mm
Slots | 1
Size | Neck 1200 mm × 1 slots
Location | Closed Ceiling
Description | 1200 mm neck length with 1 slots | 1200 mm neck length | 1 slots
Discharge direction '110.2'
with side flanges
with two end flanges
fixing by others; without accessories
| profile powder coated to RAL9003 with black barrels | RAL9003 | black
no connection box
Format
0 | Slots | 200
1 | Selected Airflow [L/s/m] | 100
2 | Airflow @ Max Static Pressure[L/s/m] | 95
3 | Min Selected Airflow [L/s/m] | 100
4 | Min Permissible Airflow [L/s/m] | 33
5 | Min % Turndown to | 1 | 100
6 | Min Permissible % Turndown to | 0.33
7 | Max Static Pressure (Pa) | 16.7
8 | Max Total Pressure (Pa) | 23.5
9 | Max Permissible Pressure (Pa) | 15
10 | Sound Power Level (dBA) | 45.7
11 | Sound Pressure Level (NC) | 30.7
12 | Heating Centre Zones for Air Direction 'A' [K] | ≈ 0.0
13 | heating Perimeter | ≈ 0.0
14 | Max C/L Distance (m) | 4.1
15 | Max Centre Z C/L Distance (m) | 12.1
16 | Min C/L Distance (m) | 2.5
17 | Min Diffuser Height (m) | 7.4
18 | Air Pattern Setting | 10.2
19 | Mean Room Air V | 89.7
20 | Draught Rating | 2.3
21 | PPD | 5.66
22 | PMV | 3.33
23 | PPD Class | DN150
24 | Nominal Spigot Size | 0
25 |  | FALSE
dt | -12
room temp | #REF!
dist type selection | 1
height | 2.5
Units | L/s | L/s
Summary
Text
Airflow | 100 L/s @ 23.5 Pa total (16.7 Pa static)
Min airflow | 100 L/s (100% turndown to) @ ΔT = -12 K
Heating non vertical | + ≈ 0.0 K for perimeter zones; + ≈ 0.0 K for centre zones
Suggested Air Direction Setting | Discharge barrels set to 110.2
Acoustic
SWL | 45.7 dB(A)/m
SPL | 30.7 NC/m
Recommended Plenum Box Spigot Diameter per (1200 mm length) | 0 mm
Comfort
ADPI | ≥ 80%
Mean Room Air Velocity | 89.7 m/s
Mean Draught Rating | #REF!
Mean PPD | 566%
Satisfies PPD (ISO7730) | Category DN150
Mean PMV * | -3.33 < PMV < +3.33
Diagram
Cmin | 2.5
Cmax | 4.1
Text | C Max = 4.1 m
C Min = 2.5 m
Average
C Select | #REF! | m
| #REF! | #REF!
#REF!
box1 | C Max = 4.1 m | 1 | #REF!
box2 | C Min = 2.5 m | 2 | #REF!
box3 | #REF! | 3 | #REF!
room box | #REF!
Height | Selected Diffuser Height = 2.5 m
Min Recommended Diffuser Height = 7.4 m
Warning
L/B | ¹ Warning: Min > Max. Recommend increasing 'Turndown' or reducing 'ADPI'
Spigot | - Warning: High spigot velocity. Recommend increasing 'Neck Height'. | High | R

## Dimensions (hidden)
SMARTEMP PRODUCT SELECTION CALCULATOR
Linear Multistream Ceiling Diffuser [LMW-AD] Dimensions
Dimensions
|  |  | 1 Slot | 2 Slots | 3 Slots | 4 Slots
|  | Width Flangeless Face (Wn) | 31 | 59 | 87 | 115 | mm
|  | Width Flanged Face (Wf) | 48 | 76 | 104 | 132 | mm
|  | Width of Diffuser Throat (Wt) | 27 | 55 | 83 | 111 | mm
|  | Recommended Plenum Height A * | 200 | 255 | 300 | 325 | mm
|  | Recommended Plenum Width B * | 81 | 109 | 137 | 165 | mm
|  | Recommended Spigot Dimension D * per 1 m length | 124 | 179 | 224 | 249 | mm
|  | Recommended Spigot Dimension D * per 1.5 m length | 149 | 224 | 249 | 279 | mm
[8 empty] | * | Check exact dimension with local supplier

## Selection Summary (hidden)
MBW-FD Performance Calculator Summary
Project | <Project Name>
Diffuser Location | <Name>
Consultant | <Name>
Product | SMARTEMP MBW-FD
Multi-Stream Bar Grille with Removable Core
Size
Diffuser Location | Closed Ceiling
Summary
Selected Airflow | 100 L/s @ 23.5 Pa total (16.7 Pa static)
Min Seleted Airflow | 100 L/s (100% turndown to) @ ΔT = -12 K
Max Recommended Heating ΔT | + ≈ 0.0 K for perimeter zones; + ≈ 0.0 K for centre zones
Selected Air Discharge Setting | Discharge barrels set to 110.2
Acoustic Performance
Sound Power Level | 45.7 dB(A)/m
Sound Pressure Level ^ | 30.7 NC/m | ^ based on 10dB room absorption
Recommended Plenum Box Spigot Diameter (per 1200 mm length) | 0 mm
Comfort Performance
ADPI | ≥ 80%
Mean Room Air Velocity | 89.7 m/s
Mean Draught Rating | #REF!
Mean PPD | 566%
Satisfies PPD (ISO7730) | Category DN150
Mean PMV * | -3.33 < PMV < +3.33
* ISO7730; ASHRAE Std 55
Description | 1200 mm neck length with 1 slots
Discharge direction '110.2'
with side flanges
with two end flanges
fixing by others; without accessories
profile powder coated to RAL9003 with black barrels
no connection box
Order Code | #REF!
C Max = 4.1 m
#REF!
C Min = 2.5 m
Min Recommended Diffuser Height = 7.4 m
#REF!
Selected Diffuser Height = 2.5 m