## HSC-FD
SMARTEMP PRODUCT SELECTION CALCULATOR
Fixed Helical Swirl Diffuser [HSC-FD DN250/DN355/DN500]
Project: | <Project Name>
| Inputs | [6 empty] | Detailed Selection | [7 empty] | v 10.14 [09/2025]
| Maximum Airflow Rate | 120 |  | L/s | m³/h |  |  | Discharge Direction |  | 4 Way (360°) | [6 empty] | Specific Airflow Rate (heating) | 5 | L/s/m2 | 2 to 10 L/s/m2 (default 5 L/s/m2)
|  | = 432 | m³/h
| VAV (turndown to) | 100 | % use 100% for CAV | [5 empty] | ADPI ≥ | 90% |  | default ≥ 90%
|  | = 120 | L/s
| Maximum Permissible Static Pressure | 35 | Pa default 35 Pa | [6 empty] | Include perforated face |  | only avalable for DN355; 595x595 Face (Rv5/6; 63% open area)
Please contact Smartair Diffusion for custom perforations
| ΔT (cooling) | -12 | K -8 to -16 K (default -12 K) |  |  |  |  | Draught Rating & Heating
use -8 K for 0 K to -8 K
| Diffuser Height | 2.7 | m 2 to 5 m | [6 empty] | Average Diffuser Coverage (Rows 50-52) |  | (see 'C' Layout Diagram below)
[8 empty] | OR |  | coverage = 7.3 m
| Diffuser Neck Size | DN355 | DN250 / DN355 / DN500 | [5 empty] | Manual Coverage Distance | 8 | m | (see 'C' in Layout Diagram below)
[8 empty] | OR |  | = specfic airflow rate: 2.3 L/s/m²
Diffuser as Return Air (R/A) Inlet: | [8 empty] | Max Specific Airflow Rate | 15 | L/s/m² | ≤ 30 L/s/m²
1. R/A diffuser pressure loss to be taken as equal to supply air static pressure. | [9 empty] | average diffuser coverage 'C': 7.3 m
2. R/A diffuser sound power level is up to 2 dB(A) greater than the supply air sound power level. | [8 empty] | Room Temperature (draught rating) | 23 | °C | 20 °C to 26 °C (default 23 °C)
| Spigot Sizing | [7 empty] | Diffuser Location | Closed Ceiling |  | Freely Suspended (≥ 600 mm below ceiling)
| ASNZ Sizes (DN150; DN200; DN250; DN300; DN350; DN400) | [7 empty] | % Low Level Return (heating) | 0% |  | 0% to 100% (default 0%)
DIN Sizes (DN160; DN200; DN250; DN315; DN355; DN400)
Thermal Comfort Guide
Related Products | [7 empty] | ADPI ≥ 95%; ṽ ≤ 0.20 m/s: | Premium comfort, sedentary activity, such as in auditoria.
Smartemp HSC-AD: | for increased flow rates; optionally with thermal/electric adjustment | [6 empty] | ADPI ≥ 90%; ṽ ≤ 0.25 m/s: | High comfort near-sedentary activity, such as in board rooms, high end offices and libraries.
Smartemp LMC-AD: | for a high-induction, linear-type solution | [6 empty] | ADPI ≥ 80%; ṽ ≤ 0.29 m/s: | Good comfort near sedentary activity, such as open-plan offices and meeting rooms.
Smartemp PMW-AD: | for a high-induction, wall-mounted solution | [6 empty] | ADPI ≥ 70%; ṽ ≤ 0.33 m/s: | Standard comfort medium activity, such as in transient spaces, retail and lobbies.
| SMARTEMP HSC-FD- |  |  | DN355-R0 | DN355-R1 | DN355-R2 | DN355-R3 | DN355-R4 | DN355-R5 | DN355-R6 | Key: | Suitable | Not Suitable | Warning / Warning
Airflow | Selected Airflow |  | [L/s] | 120 | 120 | 120 | 120 | 120 | 120 | 120
| Airflow @ Selected Pressure |  | [L/s] | 239.9 | 204.2 | 174.1 | 129.2 | 97 | 64.4 | 45.7
| Selected Min Airflow (Turndown To) |  | [L/s] | 120 | 120 | 120 | 120 | 120 | 120 | 120
| Min Permissible Airflow |  | [L/s] | 47.8 | 41.6 | 34.1 | 26.4 | 19.4 | 13.5 | 9.5
| Selected Turndown to % |  |  | 100% | 100% | 100% | 100% | 100% | 100% | 100%
| Min Permissible % Turndown to |  |  | 39.9% | 34.7% | 28.5% | 22% | 16.2% | 11.2% | 7.9% | [5 empty] | `
Pressure* | Static Pressure @ 100% Airflow |  | [Pa] | 8.8 | 12.1 | 16.6 | 30.2 | 53.6 | 121.5 | 241.6 | * Values valid for diffuser including side-entry plenum box with round spigot (refer to woksheet 'Notes & Drawings HSC-FD')
| Total Pressure @ 100% Airflow |  | [Pa] | 12.4 | 15.7 | 20.3 | 33.8 | 57.2 | 125.1 | 245.3
| Max Selected Static Pressure |  | [Pa] | 35 | 35 | 35 | 35 | 35 | 35 | 35
Acoustics | Sound Power Level |  | [dB(A)] | 27.2 | 32 | 37 | 40.8 | 46 | 54 | 60.1
| Sound Pressure Level* |  | [NC] | 12.2 | 17 | 22 | 25.8 | 31 | 39 | 45.1 | * Based on 10 dB(A) room absorption
Heating | Max Recommended Heating ΔT (Centre Zone) |  | [K] | 9.7 | 10.2 | 11.4 | 12.7 | 14.2 | 15.7 | 17.6 | Heating valid for specific flowrate of 2.3 L/s/m² (see Cells K17:K21) at 2.7 m height.
| Max Recommended Heating ΔT (Perimeter) |  | [K] | 6.5 | 6.8 | 7.6 | 8.4 | 9.5 | 10.5 | 11.7
Distances & Layout | Max Coverage 'Cmax' (for Centre Zones) |  | [m] | 12.7 | 13 | 13.3 | 14 | 15.3 | 18.8 | 22.9
| Max Coverage 'Cmax' (for Perimeter Zones) |  | [m] | 11.5 | 11.6 | 12 | 12.6 | 13.8 | 17 | 22.9
| Min Coverage 'Cmin' |  | [m] | 2.5 | 2.6 | 2.6 | 2.7 | 2.9 | 3.4 | 4.5
| Min Recommended Diffuser Height |  | [m] | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4
Comfort | Mean Room Air Velocity |  | [m/s] | 0.1 | 0.1 | 0.1 | 0.11 | 0.11 | 0.12 | 0.13
| Mean Draught Rating |  | DR | 7.7% | 7.9% | 8.2% | 8.6% | 9.3% | 10.4% | 11.8%
| Mean PPD |  |  | 5.2% | 5.3% | 5.4% | 5.5% | 5.8% | 6.2% | 6.6% | Comfort criteria for specific airflow rate of 2.3 L/s/m² (see Cells K17:K21) and room temperature of 23°C (Cell M23)
| Satisfies PPD Category |  | ISO7733 | A | A | A | A | A | B | B | "
| ¦PMV¦ |  | ISO7730; ASHRAE Std 55 | < 0.2 | < 0.2 | < 0.2 | < 0.2 | < 0.2 | < 0.2 | < 0.3
Plenum Box | Standard Plenum Box Spigot Dia. |  | [mm] | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | See 'Plenum Box Details' worksheet for spigot and plenum box details and other sizes
| 250mm Low Profile Plenum Box Spigot Dia. |  | [mm] | DN300 | DN300 | DN300 | DN300 | DN300 | DN300 | DN300 | Refer to 'Notes' worksheet for selection tool notes
Product Selection & Code Generator
| Select reducer to create order code |  |  | R0 | R1 | R2 | R3 | R4 | R5 | R6 | return air | * indicates standard/default option
| Face Shape |  |  | R1: □ 595 mm square face*; R3: ø 500 mm circular face; R5: custom face size |  | □ 595 mm square face
| Discharge Direction |  |  | R2: 4 Way (360°); R3: selected in cell M9 |  | - see cell M9
| Perforated face |  |  | R2: Perforated plate (cell L13); R3: is not selected |  | - see cell L13
| Colour |  |  | R1: RAL9003* (signal white); R3: RAL9005 (jet black); R5: other |  | powder coated
| Connection Box |  |  | R0: No Connection Box *; R2: Insulated box with magnetic fastener & cap; R5: Insulated box with threaded rod fastener and cap |  | No connection box
| Order Code |  |  | R0: SMARTEMP HSC-FD-DN355-S595-R0-4w-P0-RAL9003-0 |  | - more detailed options available in the HSC-FD product brochure
go to 'Selection Summary' for a printable summary of the selection
|  |  |  | R2: click to see product on smartair.asia |  |  |  |  | Copyright © 2020 SMARTAIR DIFFUSION
Group Box 25
26
Group Box 30
Group Box 58
Group Box 73
Group Box 43
Group Box 65
Group Box 717
Group Box 31

## HSC-FD Equations (hidden)
Units
| Unit Type | 1 | [L/s] | L/s
| Unit Multiplier | 1 | L/s/m²
| Airflow Rate | 120
| Converted Flowrate | = 432 | m³/h
Input Values
| Neck Size | DN355 |  | mm | [6 empty] | Max Airflow
| Airflow Rate - Converted | 120 |  | L/s | [6 empty] | Max Recommended Airflow (L/s)
| VAV | 100 |  | % | [6 empty] | Min Airflow (L/s)
| Max Static Pressure | 35 |  | Pa | [6 empty] | Min P Airflow
| dT (cooling) | -12 |  | K | [6 empty] | Min % Airflow
| Room Height | 2.7 |  | m | [6 empty] | Min Permissible % TD to
| Discharge Direction | 4 Way (360°) | 4w | [7 empty] | Max Total Pressure (Pa)
| Spec Airflow Rate | 15 |  | L/s/m2
| ADPI | 90% | [8 empty] | Sound Power Level (dBA)
| perforated plate | FALSE | [8 empty] | Sound Pressure Level (NC)
| Low level return | 0 | [8 empty] | Max Permissible ΔT (heating) (K)
| freely suspended | 1
| Room Temp | 23 |  | C
| Diffuser dist setting | 1
| manual diffuser dist | 8 |  | m | [6 empty] | H_min (m)
C_min (m)
| Input Pre Calcs | [9 empty] | C_max (m)
| Neck Size | 355
| Airflow Rate -4w equ | 120 |  | afr = afr *(4/discharge direction)
| VAV | 1
| Max Static Pressure | 35
| dT (cooling) | 12 | for @ velocity use '-8' for values 0 and -8 K
| Room Height | 2.7
| Discharge Direction | 4
| Spec Airflow Rate for heating | 2.3
| ADPI | 90
| Local Velocity | 0.25
| Perf-plate pressure | 1
| Perf Plate Vmin | 1
| Perf-plate noise | 0
| V_turndown | 120 |  | v_td=afr*vav
| V_turndown - 4 way equiv | 120
| Low Level Return | 1
| free susp | FALSE
| Free Susp (heat) | 1
| Free Susp (Hmin) | 1
| Free susp (Cmin) | 1
| Free Susp (Cmax) | 1
| 2-Way 180 deg | 1
Cmin Table
Target Q''
| H | ax | ^b | Q''
| 2.7 | 4510 | 2.2693 | 194.0536
| 4 | 3884 | 2.2426 | 173.4201
| 10.0001 | 3435 | 2.2754 | 146.5546
|  | Ax | ^b
| 2.7 | 235.858 | -0.20897 | 191.6493 | W/m2
v'
| v' & Vmax | 15.9708
| v' & Vmin | 19.9708
| v'' +correction factor | 4
Cmax Table
| adpi | v' @Vmax | v' @ Vmin |  | Hfactor @ Vmax | Hfactor @ Vmin
| 95% | 0.955 | 1.27 |  | 5.317 | 4.4309
| 90% | 0.75 | 1 |  | 6 | 5
| 85% | 0.60762 | 0.80827 |  | 6.6828 | 5.5685
| 80% | 0.5 | 0.66 |  | 7.3659 | 6.1383
| 70% | 0.35 | 0.47 |  | 8.7318 | 7.2765
| v' & Vmax | 0.75 |  | at ADPI | 6 | factor * room height
| v' & Vmin | 1 |  |  | 5
Cmax-Centre Zone Table
| adpi | v' @Vmax | v' @ Vmin |  | Hfactor @ Vmax | Hfactor @ Vmin
| 95% | 0.75963 | 1.0121 |  | 5.317 | 4.4309
| 90% | 0.60762 | 0.80827 |  | 6 | 5
| 85% | 0.48872 | 0.6503 |  | 6.6828 | 5.5685
| 80% | 0.40294 | 0.53818 |  | 7.3659 | 6.1383
| 70% | 0.33072 | 0.45147 |  | 8.7318 | 7.2765
| v' & Vmax | 0.60762 |  | at ADPI | 6 | factor * room height
| v' & Vmin | 0.80827 |  |  | 5
COVERAGE AND RADIUS - multipliers (discharge patttern)
| R multiplier | 0.5
| Area multiplier | 4 | A= M*R^2
| R to Coverage Conversion | 2
| Area multiplier from C | 1 | A= M * C^2
| 250 | [44 empty] | 355 | [41 empty] | DN500
| 250 Reducer 0 | [6 empty] | 250 Reducer 1 | [6 empty] | 250 Reducer 2 | [6 empty] | 250 Reducer 3 | [5 empty] | 250 Reducer 4 | [5 empty] | 250 Reducer 5 | [5 empty] | 250 Reducer 6 | [5 empty] | Reducer 0 | [5 empty] | Reducer 1 | [5 empty] | Reducer 2 | [5 empty] | Reducer 3 | [5 empty] | Reducer 4 | [5 empty] | Reducer 5 | [5 empty] | Reducer 6 | [5 empty] | Reducer 0 | [5 empty] | Reducer 1 | [5 empty] | Reducer 2 | [5 empty] | Reducer 3 | [5 empty] | Reducer 4 | [5 empty] | Reducer 5
| data.Flowrate | 110 | L/s | P Static | 31.94 | Pa |  | data.Flowrate | 96.11 | L/s | P Static | 31 | Pa |  | data.Flowrate | 78.845 | L/s | P Static | 28.7 | Pa |  | data.Flowrate | 61.005 | L/s | P Static | 31.2 | Pa | data.Flowrate | 44.89 | L/s | P Static | 30 | Pa | data.Flowrate | 31.08 | L/s | P Static | 32.6 | Pa | data.Flowrate | 21.87 | L/s | P Static | 32.1 | Pa | data.Flowrate | 221 | L/s | P Static | 29.7 | Pa | data.Flowrate | 192.22 | L/s | Vmin | 31 | Pa | data.Flowrate | 157.69 | L/s | Vmin | 28.7 | Pa | data.Flowrate | 122.01 | L/s | P static | 31.2 | Pa | data.Flowrate | 89.78 | L/s | Vmin | 30 | Pa | data.Flowrate | 62.16 | L/s | Vmin | 32.6 | Pa | data.Flowrate | 43.74 | L/s | P static | 32.1 | Pa | data.Flowrate | 440 | L/s | P static | 26.4 | Pa | data.Flowrate | 398 | L/s | P static | 28 | Pa | data.Flowrate | 358 | L/s | Vmin | 29.3 | Pa | data.Flowrate | 295 | L/s | Vmin | 28.8 | Pa | data.Flowrate | 220 | L/s | Vmin | 29.7 | Pa | data.Flowrate | 151 | L/s | Vmin | 29.2 | Pa
| data.If.Perforated | 110 | L/s |  | 31.94 | Pa |  | data.If.Perforated | 96.11 | L/s |  | 31 | Pa |  | data.If.Perforated | 78.845 | L/s |  | 28.7 | Pa |  | data.If.Perforated | 61.005 | L/s |  | 31.2 | Pa | data.If.Perforated | 44.89 | L/s |  | 30 | Pa | data.If.Perforated | 31.08 | L/s |  | 32.6 | Pa | data.If.Perforated | 21.87 | L/s |  | 32.1 | Pa | data.Perforated | 221 | L/s |  | 29.7 | Pa | data.Perforated | 192.22 | L/s |  | 31 | Pa | data.Perforated | 157.69 | L/s |  | 28.7 | Pa | data.Perforated | 122.01 | L/s |  | 31.2 | Pa | data.Perforated | 89.78 | L/s |  | 30 | Pa | data.Perforated | 62.16 | L/s | 28 | 32.6 | Pa | data.Perforated | 43.74 | L/s |  | 32.1 | Pa | data.Perforated | 440 | L/s |  | 26.4 | Pa | data.Perforated | 398 | L/s |  | 28 | Pa | data.Perforated | 358 | L/s |  | 29.3 | Pa | data.Perforated | 295 | L/s |  | 28.8 | Pa | data.Perforated | 220 | L/s |  | 29.7 | Pa | data.Perforated | 151 | L/s |  | 29.2 | Pa
| Static Pressure | 38.0112 | [5 empty] | Static Pressure | 48.3267 | [5 empty] | Static Pressure | 66.4808 | [5 empty] | Static Pressure | 120.7219 |  |  |  |  | Static Pressure | 214.3801 |  |  |  |  | Static Pressure | 485.9796 |  |  |  |  | Static Pressure | 966.429 |  |  |  |  | Static Pressure | 8.7566 |  |  |  |  | Static Pressure | 12.0817 |  |  |  |  | Static Pressure | 16.6202 |  |  |  |  | Static Pressure | 30.1805 |  |  |  |  | Static Pressure | 53.595 |  |  |  |  | Static Pressure | 121.4949 |  |  |  |  | Static Pressure | 241.6073 |  |  |  |  | Static Pressure | 1.9636 |  |  |  |  | Static Pressure | 2.5454 |  |  |  |  | Static Pressure | 3.292 |  |  |  |  | Static Pressure | 4.7655 |  |  |  |  | Static Pressure | 8.8364 |  |  |  |  | Static Pressure | 18.4413
| Total Pressure @ Flowrate | 41.6549 | [5 empty] | Total Pressure @ Flowrate | 51.9703 | [5 empty] | Total Pressure @ Flowrate | 70.1244 | [5 empty] | Total Pressure @ Flowrate | 124.3656 |  |  |  |  | Total Pressure @ Flowrate | 218.0238 |  |  |  |  | Total Pressure @ Flowrate | 489.6233 |  |  |  |  | Total Pressure @ Flowrate | 970.0727 |  |  |  |  | Total Pressure @ Flowrate | 12.4002 |  |  |  |  | Total Pressure @ Flowrate | 15.7253 |  |  |  |  | Total Pressure @ Flowrate | 20.2638 |  |  |  |  | Total Pressure @ Flowrate | 33.8241 |  |  |  |  | Total Pressure @ Flowrate | 57.2387 |  |  |  |  | Total Pressure @ Flowrate | 125.1386 |  |  |  |  | Total Pressure @ Flowrate | 245.2509 |  |  |  |  | Total Pressure @ Flowrate | 5.6073 |  |  |  |  | Total Pressure @ Flowrate | 6.189 |  |  |  |  | Total Pressure @ Flowrate | 6.9357 |  |  |  |  | Total Pressure @ Flowrate | 8.4092 |  |  |  |  | Total Pressure @ Flowrate | 12.48 |  |  |  |  | Total Pressure @ Flowrate | 22.0849
| Flowrate @ MaxP | 115.1488 | [5 empty] | Flowrate @ MaxP | 102.1226 | [5 empty] | Flowrate @ MaxP | 87.0697 | [5 empty] | Flowrate @ MaxP | 64.6133 |  |  |  |  | Flowrate @ MaxP | 48.4867 |  |  |  |  | Flowrate @ MaxP | 32.2037 |  |  |  |  | Flowrate @ MaxP | 22.8365 |  |  |  |  | Flowrate @ MaxP | 239.9098 |  |  |  |  | Flowrate @ MaxP | 204.2451 |  |  |  |  | Flowrate @ MaxP | 174.1395 |  |  |  |  | Flowrate @ MaxP | 129.2267 |  |  |  |  | Flowrate @ MaxP | 96.9735 |  |  |  |  | Flowrate @ MaxP | 64.4075 |  |  |  |  | Flowrate @ MaxP | 45.6731 |  |  |  |  | Flowrate @ MaxP | 506.6228 |  |  |  |  | Flowrate @ MaxP | 444.9775 |  |  |  |  | Flowrate @ MaxP | 391.276 |  |  |  |  | Flowrate @ MaxP | 325.2069 |  |  |  |  | Flowrate @ MaxP | 238.8243 |  |  |  |  | Flowrate @ MaxP | 165.3178
| V_min | 23.8157 | [5 empty] | V_min | 20.8084 | [5 empty] | V_min | 17.0704 | [5 empty] | V_min | 13.208 |  |  |  |  | V_min | 9.719 |  |  |  |  | V_min | 6.729 |  |  |  |  | V_min | 4.735 |  |  |  |  | V_min | 47.8479 |  |  |  |  | V_min | 41.6169 |  |  |  |  | V_min | 34.1409 |  |  |  |  | V_min | 26.4159 |  |  |  |  | V_min | 19.4379 |  |  |  |  | V_min | 13.458 |  |  |  |  | V_min | 9.47 |  |  |  |  | V_min | 95.2628 |  |  |  |  | V_min | 86.1695 |  |  |  |  | V_min | 77.5093 |  |  |  |  | V_min | 63.8694 |  |  |  |  | V_min | 47.6314 |  |  |  |  | V_min | 32.6925
| Min % turndown to | 0.19846 | [5 empty] | Min % turndown to | 0.1734 | [5 empty] | Min % turndown to | 0.14225 | [5 empty] | Min % turndown to | 0.11007 |  |  |  |  | Min % turndown to | 0.080991 |  |  |  |  | Min % turndown to | 0.056075 |  |  |  |  | Min % turndown to | 0.039458 |  |  |  |  | Min % turndown to | 0.39873 |  |  |  |  | Min % turndown to | 0.34681 |  |  |  |  | Min % turndown to | 0.28451 |  |  |  |  | Min % turndown to | 0.22013 |  |  |  |  | Min % turndown to | 0.16198 |  |  |  |  | Min % turndown to | 0.11215 |  |  |  |  | Min % turndown to | 0.078917 |  |  |  |  | Min % turndown to | 0.79386 |  |  |  |  | Min % turndown to | 0.71808 |  |  |  |  | Min % turndown to | 0.64591 |  |  |  |  | Min % turndown to | 0.53224 |  |  |  |  | Min % turndown to | 0.39693 |  |  |  |  | Min % turndown to | 0.27244
| SWL | 44.6244 |  | 13.415 | -4.1778 |  |  | SWL | 47.3244 |  | 13.415 | -4.6988 |  |  | SWL | 50.849 |  | 13.4 | -5.3896 |  |  | SWL | 57.5503 |  | 13.4 | -6.6825 |  | SWL | 64.0005 |  | 13.4 | -7.9274 |  | SWL | 73.1884 |  | 13.4 | -9.7062 |  | SWL | 80.9009 |  | 13.4 | -11.2054 |  | SWL | 27.2367 |  | 14.752 | -4.7723 |  | SWL | 31.9502 |  | 16.69 | -9.6361 |  | SWL | 37.0186 |  | -0.000456 | 0.343 | 2.425 | SWL | 40.754 |  | -0.0006066 | 0.3922 | 2.425 | SWL | 46.0134 |  | -0.0005956 | 0.4122 | 5.126 | SWL | 54.0008 |  | -0.001488 | 0.5994 | 3.5 | SWL | 60.136 |  | -0.003135 | 0.8437 | 4.036 | SWL | 8.3727 |  | 15.353 | -1.9875 |  | SWL | 11.3006 |  | 16.463 | -4.0805 |  | SWL | 22.1738 |  | -0.0001339 | 0.1832 | 2.118 | SWL | 24.1202 |  | -0.0001868 | 0.217 | 0.7701 | SWL | 27.8611 |  | -0.0001993 | 0.23 | 3.131 | SWL | 33.809 |  | -0.000335 | 0.2805 | 4.973
| SPL | 29.6244 | [5 empty] | SPL | 32.3244 | [5 empty] | SPL | 35.849 | [5 empty] | SPL | 42.5503 |  |  |  |  | SPL | 49.0005 |  |  |  |  | SPL | 58.1884 |  |  |  |  | SPL | 65.9009 |  |  |  |  | SPL | 12.2367 |  |  |  |  | SPL | 16.9502 |  |  |  |  | SPL | 22.0186 |  |  |  |  | SPL | 25.754 |  |  |  |  | SPL | 31.0134 |  |  |  |  | SPL | 39.0008 |  |  |  |  | SPL | 45.136 |  |  |  |  | SPL | -6.6273 |  |  |  |  | SPL | -3.6994 |  |  |  |  | SPL | 7.1738 |  |  |  |  | SPL | 9.1202 |  |  |  |  | SPL | 12.8611 |  |  |  |  | SPL | 18.809
| Hmin | [6 empty] | Hmin | [6 empty] | Hmin | [6 empty] | Hmin | [5 empty] | Hmin | [5 empty] | Hmin | [5 empty] | Hmin | [5 empty] | Hmin
| Factor | 5.1741 |  | -9.02e-05 | 0.0577 | -0.451 |  | Factor | 5.1741 |  | -9.02e-05 | 0.0577 | -0.451 |  | Factor | 5.1741 |  | -9.02e-05 | 0.0577 | -0.451 |  | Factor | 5.1741 |  | -9.02e-05 | 0.0577 | -0.451 | Factor | 5.1741 |  | -9.02e-05 | 0.0577 | -0.451 | Factor | 5.1741 |  | -9.02e-05 | 0.0577 | -0.451 | Factor | 5.1741 |  | -9.02e-05 | 0.0577 | -0.451 | Factor | 5.1741 |  | -9.02e-05 | 0.0577 | -0.451 | Factor | 5.1741 |  | -9.02e-05 | 0.0577 | -0.451 | Factor | 5.1741 |  | -9.02e-05 | 0.0577 | -0.451 | Factor | 5.1741 |  | -9.02e-05 | 0.0577 | -0.451 | Factor | 5.1741 |  | -9.02e-05 | 0.0577 | -0.451 | Factor | 5.1741 |  | -9.02e-05 | 0.0577 | -0.451 | Factor | 5.1741 |  | -9.02e-05 | 0.0577 | -0.451 | Factor | 2.7696 |  | -1.563e-05 | 0.02321 | 0.2095 | Factor | 2.7696 |  | -1.563e-05 | 0.02321 | 0.2095 | Factor | 2.7696 |  | -1.563e-05 | 0.02321 | 0.2095 | Factor | 2.7696 |  | -1.563e-05 | 0.02321 | 0.2095 | Factor | 2.7696 |  | -1.563e-05 | 0.02321 | 0.2095 | Factor | 2.7696 |  | -1.563e-05 | 0.02321 | 0.2095
| H_min_90 | 2.2723 | [5 empty] | H_min_90 | 2.2723 | [5 empty] | H_min_90 | 2.2723 | [5 empty] | H_min_90 | 2.2723 |  |  |  |  | H_min_90 | 2.2723 |  |  |  |  | H_min_90 | 2.2723 |  |  |  |  | H_min_90 | 2.2723 |  |  |  |  | H_min_90 | 2.3723 |  |  |  |  | H_min | 2.3723 |  |  | 0.0333 | 2.2 | H_min | 2.3723 |  |  | 0.0333 | 2.2 | H_min | 2.3723 |  |  | 0.0333 | 2.2 | H_min | 2.3723 |  |  | 0.0333 | 2.2 | H_min | 2.3723 |  |  | 0.0333 | 2.2 | H_min | 2.3723 |  |  | 0.0333 | 2.2 | H_min | 2.3922 |  |  | 0.0333 | 2.3 | H_min | 2.3922 |  |  | 0.0333 | 2.3 | H_min | 2.3922 |  |  | 0.0333 | 2.3 | H_min | 2.3922 |  |  | 0.0333 | 2.3 | H_min | 2.3922 |  |  | 0.0333 | 2.3 | H_min | 2.3922 |  |  | 0.0333 | 2.3
| ADPI | [6 empty] | ADPI | [37 empty] | ADPI | [5 empty] | ADPI | [5 empty] | ADPI | [5 empty] | ADPI | [5 empty] | ADPI | [5 empty] | ADPI | [5 empty] | ADPI | [5 empty] | ADPI | [5 empty] | ADPI | [5 empty] | ADPI | [5 empty] | ADPI | [5 empty] | ADPI | [5 empty] | ADPI
| H_min | 95% | 2.3723 |  |  |  |  | H_min | 95% | 2.3723 |  |  |  |  | H_min | 95% | 2.3723 |  |  |  |  | H_min | 95% | 2.3723 |  |  |  | H_min | 95% | 2.3723 |  |  |  | H_min | 95% | 2.3723 |  |  |  | H_min | 95% | 2.3723 |  |  |  | H_min | 95% | 2.4723 |  |  |  | H_min | 95% | 2.4723 |  |  |  | H_min | 95% | 2.4723 |  |  |  | H_min | 95% | 2.4723 |  |  |  | H_min | 95% | 2.4723 |  |  |  | H_min | 95% | 2.4723 |  |  |  | H_min | 95% | 2.4723 |  |  |  | H_min | 95% | 2.4922 |  |  |  | H_min | 95% | 2.4922 |  |  |  | H_min | 95% | 2.4922 |  |  |  | H_min | 95% | 2.4922 |  |  |  | H_min | 95% | 2.4922 |  |  |  | H_min | 95% | 2.4922
|  | 90% | 2.2723 | [5 empty] | 90% | 2.2723 | [5 empty] | 90% | 2.2723 | [5 empty] | 90% | 2.2723 |  |  |  |  | 90% | 2.2723 |  |  |  |  | 90% | 2.2723 |  |  |  |  | 90% | 2.2723 |  |  |  |  | 90% | 2.3723 |  |  |  |  | 90% | 2.3723 |  |  |  |  | 90% | 2.3723 |  |  |  |  | 90% | 2.3723 |  |  |  |  | 90% | 2.3723 |  |  |  |  | 90% | 2.3723 |  |  |  |  | 90% | 2.3723 |  |  |  |  | 90% | 2.3922 |  |  |  |  | 90% | 2.3922 |  |  |  |  | 90% | 2.3922 |  |  |  |  | 90% | 2.3922 |  |  |  |  | 90% | 2.3922 |  |  |  |  | 90% | 2.3922
|  | 85% | 2.2223 | [5 empty] | 85% | 2.2223 | [5 empty] | 85% | 2.2223 | [5 empty] | 85% | 2.2223 |  |  |  |  | 85% | 2.2223 |  |  |  |  | 85% | 2.2223 |  |  |  |  | 85% | 2.2223 |  |  |  |  | 85% | 2.3223 |  |  |  |  | 85% | 2.3223 |  |  |  |  | 85% | 2.3223 |  |  |  |  | 85% | 2.3223 |  |  |  |  | 85% | 2.3223 |  |  |  |  | 85% | 2.3223 |  |  |  |  | 85% | 2.3223 |  |  |  |  | 85% | 2.3422 |  |  |  |  | 85% | 2.3422 |  |  |  |  | 85% | 2.3422 |  |  |  |  | 85% | 2.3422 |  |  |  |  | 85% | 2.3422 |  |  |  |  | 85% | 2.3422
|  | 80% | 2.1723 | [5 empty] | 80% | 2.1723 | [5 empty] | 80% | 2.1723 | [5 empty] | 80% | 2.1723 |  |  |  |  | 80% | 2.1723 |  |  |  |  | 80% | 2.1723 |  |  |  |  | 80% | 2.1723 |  |  |  |  | 80% | 2.2723 |  |  |  |  | 80% | 2.2723 |  |  |  |  | 80% | 2.2723 |  |  |  |  | 80% | 2.2723 |  |  |  |  | 80% | 2.2723 |  |  |  |  | 80% | 2.2723 |  |  |  |  | 80% | 2.2723 |  |  |  |  | 80% | 2.2922 |  |  |  |  | 80% | 2.2922 |  |  |  |  | 80% | 2.2922 |  |  |  |  | 80% | 2.2922 |  |  |  |  | 80% | 2.2922 |  |  |  |  | 80% | 2.2922
|  | 70% | 2.0723 | [5 empty] | 70% | 2.0723 | [5 empty] | 70% | 2.0723 | [5 empty] | 70% | 2.0723 |  |  |  |  | 70% | 2.0723 |  |  |  |  | 70% | 2.0723 |  |  |  |  | 70% | 2.0723 |  |  |  |  | 70% | 2.1723 |  |  |  |  | 70% | 2.1723 |  |  |  |  | 70% | 2.1723 |  |  |  |  | 70% | 2.1723 |  |  |  |  | 70% | 2.1723 |  |  |  |  | 70% | 2.1723 |  |  |  |  | 70% | 2.1723 |  |  |  |  | 70% | 2.1922 |  |  |  |  | 70% | 2.1922 |  |  |  |  | 70% | 2.1922 |  |  |  |  | 70% | 2.1922 |  |  |  |  | 70% | 2.1922 |  |  |  |  | 70% | 2.1922
| Hmin | 2.2723 | 2.2723 |  |  |  |  | Hmin | 2.2723 | 2.2723 |  |  |  |  | Hmin | 2.2723 | 2.2723 |  |  |  |  | Hmin | 2.2723 | 2.2723 |  |  |  | Hmin | 2.2723 | 2.2723 |  |  |  | Hmin | 2.2723 | 2.2723 |  |  |  | Hmin | 2.2723 | 2.2723 |  |  |  | Hmin | 2.3723 | 2.3723 |  |  |  | Hmin | 2.3723 | 2.3723 |  |  |  | Hmin | 2.3723 | 2.3723 |  |  |  | Hmin | 2.3723 | 2.3723 |  |  |  | Hmin | 2.3723 | 2.3723 |  |  |  | Hmin | 2.3723 | 2.3723 |  |  |  | Hmin | 2.3723 | 2.3723 |  |  |  | Hmin | 2.3922 | 2.3922 |  |  |  | Hmin | 2.3922 | 2.3922 |  |  |  | Hmin | 2.3922 | 2.3922 |  |  |  | Hmin | 2.3922 | 2.3922 |  |  |  | Hmin | 2.3922 | 2.3922 |  |  |  | Hmin | 2.3922 | 2.3922
| Distance Selection | [6 empty] | Distance Selection | [6 empty] | Distance Selection | [6 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection
| Vmax | 110 | [5 empty] | Vmax | 96.11 | [5 empty] | Vmax | 78.845 | [5 empty] | Vmax | 61.005 |  |  |  |  | Vmax | 44.89 |  |  |  |  | Vmax | 31.08 |  |  |  |  | Vmax | 21.87 |  |  |  |  | Vmax | 221 |  |  |  |  | Vmax | 192.22 |  |  |  |  | Vmax | 157.69 |  |  |  |  | Vmax | 122.01 |  |  |  |  | Vmax | 89.78 |  |  |  |  | Vmax | 62.16 |  |  |  |  | Vmax | 43.74 |  |  |  |  | Vmax | 440 |  |  |  |  | Vmax | 398 |  |  |  |  | Vmax | 358 |  |  |  |  | Vmax | 295 |  |  |  |  | Vmax | 220 |  |  |  |  | Vmax | 151
| Vmin | 33 | [5 empty] | Vmin | 28.833 | [5 empty] | Vmin | 23.6535 | [5 empty] | Vmin | 18.3015 |  |  |  |  | Vmin | 13.467 |  |  |  |  | Vmin | 9.324 |  |  |  |  | Vmin | 6.561 |  |  |  |  | Vmin | 66.3 |  |  |  |  | Vmin | 57.666 |  |  |  |  | Vmin | 47.307 |  |  |  |  | Vmin | 36.603 |  |  |  |  | Vmin | 26.934 |  |  |  |  | Vmin | 18.648 |  |  |  |  | Vmin | 13.122 |  |  |  |  | Vmin | 132 |  |  |  |  | Vmin | 119.4 |  |  |  |  | Vmin | 107.4 |  |  |  |  | Vmin | 88.5 |  |  |  |  | Vmin | 66 |  |  |  |  | Vmin | 45.3
| Cmin | [6 empty] | Cmin | [6 empty] | Cmin | [6 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin
| v' @ V | 15.4513 | [5 empty] | v' @ V | 14.5504 | [5 empty] | v' @ V | 12.9881 | [5 empty] | v' @ V | 10.4448 |  |  |  |  | v' @ V | 6.4096 |  |  |  |  | v' @ V | -0.37782 |  |  |  |  | v' @ V | -9.669 |  |  |  |  | v' @ V | 18.5823 |  |  |  |  | v' @ V | 18.1177 |  |  |  |  | v' @ V | 17.3366 |  |  |  |  | v' @ V | 16.0649 |  |  |  |  | v' @ V | 14.0473 |  |  |  |  | v' @ V | 10.6536 |  |  |  |  | v' @ V | 6.008 |  |  |  |  | v' @ V | 20.1266 |  |  |  |  | v' @ V | 19.9622 |  |  |  |  | v' @ V | 19.7697 |  |  |  |  | v' @ V | 19.3606 |  |  |  |  | v' @ V | 18.5682 |  |  |  |  | v' @ V | 17.1439
| C_min | 2.7868 | [5 empty] | C_min | 2.8718 | [5 empty] | C_min | 3.0396 | [5 empty] | C_min | 3.3895 |  |  |  |  | C_min | 4.3269 |  |  |  |  | C_min | [5 empty] | C_min | [5 empty] | C_min | 2.5412 |  |  |  |  | C_min | 2.5736 |  |  |  |  | C_min | 2.6309 |  |  |  |  | C_min | 2.7331 |  |  |  |  | C_min | 2.9228 |  |  |  |  | C_min | 3.3562 |  |  |  |  | C_min | 4.4692 |  |  |  |  | C_min | 2.4418 |  |  |  |  | C_min | 2.4518 |  |  |  |  | C_min | 2.4637 |  |  |  |  | C_min | 2.4896 |  |  |  |  | C_min | 2.5422 |  |  |  |  | C_min | 2.6457
| Min Coverage | [6 empty] | R min | [6 empty] | R min | [6 empty] | R min | [5 empty] | R min | [5 empty] | R min | [5 empty] | R min | [5 empty] | R min | [5 empty] | R min | [5 empty] | R min | [5 empty] | R min | [5 empty] | R min | [5 empty] | R min | [5 empty] | R min | [5 empty] | R min | [5 empty] | R min | [5 empty] | R min | [5 empty] | R min | [5 empty] | R min | [5 empty] | R min
| v'@ V | 15.4513 | [5 empty] | v'@ V | 14.5504 | [5 empty] | v'@ V | 12.9881 | [5 empty] | v'@ V | 10.4448 |  |  |  |  | v'@ V | 6.4096 |  |  |  |  | v'@ V | -0.37782 |  |  |  |  | v'@ V | -9.669 |  |  |  |  | v'@ V | 18.5823 |  |  |  |  | v'@ V | 18.1177 |  |  |  |  | v'@ V | 17.3366 |  |  |  |  | v'@ V | 16.0649 |  |  |  |  | v'@ V | 14.0473 |  |  |  |  | v'@ V | 10.6536 |  |  |  |  | v'@ V | 6.008 |  |  |  |  | v'@ V | 20.1266 |  |  |  |  | v'@ V | 19.9622 |  |  |  |  | v'@ V | 19.7697 |  |  |  |  | v'@ V | 19.3606 |  |  |  |  | v'@ V | 18.5682 |  |  |  |  | v'@ V | 17.1439
| R min | 1.3934 | 2.7868 |  |  |  |  | R min | 1.4359 | [5 empty] | R min | 1.5198 | [5 empty] | R min | 1.6948 |  |  |  |  | R min | 2.1634 |  |  |  |  | R min | [5 empty] | R min | [5 empty] | R min | 1.2706 |  |  |  |  | R min | 1.2868 |  |  |  |  | R min | 1.3155 |  |  |  |  | R min | 1.3665 |  |  |  |  | R min | 1.4614 |  |  |  |  | R min | 1.6781 |  |  |  |  | R min | 2.2346 |  |  |  |  | R min | 1.2209 |  |  |  |  | R min | 1.2259 |  |  |  |  | R min | 1.2319 |  |  |  |  | R min | 1.2448 |  |  |  |  | R min | 1.2711 |  |  |  |  | R min | 1.3228
| Coverage Min | 2.7868 | [5 empty] | Coverage Min | 2.8718 | [5 empty] | Coverage Min | 3.0396 | [5 empty] | Coverage Min | 3.3895 |  |  |  |  | Coverage Min | 4.3269 |  |  |  |  | Coverage Min | #VALUE! |  |  |  |  | Coverage Min | #VALUE! |  |  |  |  | Coverage Min | 2.5412 |  |  |  |  | Coverage Min | 2.5736 |  |  |  |  | Coverage Min | 2.6309 |  |  |  |  | Coverage Min | 2.7331 |  |  |  |  | Coverage Min | 2.9228 |  |  |  |  | Coverage Min | 3.3562 |  |  |  |  | Coverage Min | 4.4692 |  |  |  |  | Coverage Min | 2.4418 |  |  |  |  | Coverage Min | 2.4518 |  |  |  |  | Coverage Min | 2.4637 |  |  |  |  | Coverage Min | 2.4896 |  |  |  |  | Coverage Min | 2.5422 |  |  |  |  | Coverage Min | 2.6457
| Cmax | [6 empty] | Cmax | [6 empty] | Cmax | [6 empty] | Cmax | [5 empty] | Cmax | [5 empty] | Cmax | [5 empty] | Cmax | [5 empty] | Cmax | [5 empty] | Cmax | [5 empty] | Cmax | [5 empty] | Cmax | [5 empty] | Cmax | [5 empty] | Cmax | [5 empty] | Cmax | [5 empty] | Cmax | [5 empty] | Cmax | [5 empty] | Cmax | [5 empty] | Cmax | [5 empty] | Cmax | [5 empty] | Cmax
Perimeter Zone
| v' @ V | 0.71753 | [5 empty] | v' @ V | 0.66123 | [5 empty] | v' @ V | 0.56358 | [5 empty] | v' @ V | 0.40462 |  |  |  |  | v' @ V | 0.15243 |  |  |  |  | v' @ V | -0.27179 |  |  |  |  | v' @ V | -0.85249 |  |  |  |  | v' @ V | 0.91322 |  |  |  |  | v' @ V | 0.88418 |  |  |  |  | v' @ V | 0.83536 |  |  |  |  | v' @ V | 0.75588 |  |  |  |  | v' @ V | 0.62979 |  |  |  |  | v' @ V | 0.41768 |  |  |  |  | v' @ V | 0.12733 |  |  |  |  | v' @ V | 1.0097 |  |  |  |  | v' @ V | 0.99946 |  |  |  |  | v' @ V | 0.98743 |  |  |  |  | v' @ V | 0.96186 |  |  |  |  | v' @ V | 0.91234 |  |  |  |  | v' @ V | 0.82332
| H Factor | 6.1299 | [5 empty] | H Factor | 6.3551 | [5 empty] | H Factor | 6.7457 | [5 empty] | H Factor | 7.3815 |  |  |  |  | H Factor | 8.3903 |  |  |  |  | H Factor | 10.0871 |  |  |  |  | H Factor | 12.41 |  |  |  |  | H Factor | 5.3471 |  |  |  |  | H Factor | 5.4633 |  |  |  |  | H Factor | 5.6586 |  |  |  |  | H Factor | 5.9765 |  |  |  |  | H Factor | 6.4809 |  |  |  |  | H Factor | 7.3293 |  |  |  |  | H Factor | 8.4907 |  |  |  |  | H Factor | 4.961 |  |  |  |  | H Factor | 5.0022 |  |  |  |  | H Factor | 5.0503 |  |  |  |  | H Factor | 5.1525 |  |  |  |  | H Factor | 5.3506 |  |  |  |  | H Factor | 5.7067
| C_max!=2.7 | 12.9321 | [5 empty] | C_max!=2.8 | 13.4715 | [5 empty] | C_max!=2.9 | 14.5919 | [5 empty] | C_max!=2.10 | 17.2212 |  |  |  |  | C_max!=2.11 | 28.0581 |  |  |  |  | C_max!=2.12 | #NUM! |  |  |  |  | C_max!=2.13 | #NUM! |  |  |  |  | C_max<=2.8 | 11.4631 |  |  |  |  | C_max<=2.9 | 11.6498 |  |  |  |  | C_max<=2.10 | 11.9854 |  |  |  |  | C_max<=2.11 | 12.5998 |  |  |  |  | C_max<=2.12 | 13.8037 |  |  |  |  | C_max<=2.13 | 16.95 |  |  |  |  | C_max<=2.14 | 30.6994 |  |  |  |  | C_max<=2.15 | 10.9015 |  |  |  |  | C_max<=2.16 | 10.9574 |  |  |  |  | C_max<=2.17 | 11.024 |  |  |  |  | C_max<=2.18 | 11.1695 |  |  |  |  | C_max<=2.19 | 11.4687 |  |  |  |  | C_max<=2.20 | 12.0727
| C_max_roomheight | 16.5506 | [5 empty] | C_max_roomheight | 17.1588 | [5 empty] | C_max_roomheight | 18.2133 | [5 empty] | C_max_roomheight | 19.9301 |  |  |  |  | C_max_roomheight | 22.6538 |  |  |  |  | C_max_roomheight | 27.2353 |  |  |  |  | C_max_roomheight | 33.5069 |  |  |  |  | C_max_roomheight | 14.4372 |  |  |  |  | C_max_roomheight | 14.7508 |  |  |  |  | C_max_roomheight | 15.2781 |  |  |  |  | C_max_roomheight | 16.1365 |  |  |  |  | C_max_roomheight | 17.4983 |  |  |  |  | C_max_roomheight | 19.7891 |  |  |  |  | C_max_roomheight | 22.9249 |  |  |  |  | C_max_roomheight | 13.3948 |  |  |  |  | C_max_roomheight | 13.5058 |  |  |  |  | C_max_roomheight | 13.6358 |  |  |  |  | C_max_roomheight | 13.9119 |  |  |  |  | C_max_roomheight | 14.4468 |  |  |  |  | C_max_roomheight | 15.4081
| C_max | 12.9321 | final selection |  |  |  |  | C_max | 13.4715 | final selection |  |  |  |  | C_max | 14.5919 | final selection |  |  |  |  | C_max | 17.2212 | final selection |  |  |  | C_max | 22.6538 | final selection |  |  |  | C_max | #NUM! | final selection |  |  |  | C_max | #NUM! | final selection |  |  |  | C_max | 11.4631 | final selection |  |  |  | C_max | 11.6498 | final selection |  |  |  | C_max | 11.9854 | final selection |  |  |  | C_max | 12.5998 | final selection |  |  |  | C_max | 13.8037 | final selection |  |  |  | C_max | 16.95 | final selection |  |  |  | C_max | 22.9249 | final selection |  |  |  | C_max | 10.9015 | final selection |  |  |  | C_max | 10.9574 | final selection |  |  |  | C_max | 11.024 | final selection |  |  |  | C_max | 11.1695 | final selection |  |  |  | C_max | 11.4687 | final selection |  |  |  | C_max | 12.0727 | final selection
| Coverage max - Perimeter Zone | [6 empty] | R max - Perimeter Zone | [6 empty] | R max - Perimeter Zone | [6 empty] | R max - Perimeter Zone | [5 empty] | R max - Perimeter Zone | [5 empty] | R max - Perimeter Zone | [5 empty] | R max - Perimeter Zone | [5 empty] | R max - Perimeter Zone | [5 empty] | R max - Perimeter Zone | [5 empty] | R max - Perimeter Zone | [5 empty] | R max - Perimeter Zone | [5 empty] | R max - Perimeter Zone | [5 empty] | R max - Perimeter Zone | [5 empty] | R max - Perimeter Zone | [5 empty] | R max - Perimeter Zone | [5 empty] | R max - Perimeter Zone | [5 empty] | R max - Perimeter Zone | [5 empty] | R max - Perimeter Zone | [5 empty] | R max - Perimeter Zone | [5 empty] | R max - Perimeter Zone
| v' @ V | 0.71753 | v' based on ratios therefore based on 4-way equivalent |  |  |  |  | v' @ V | 0.66123 | [5 empty] | v' @ V | 0.56358 | [5 empty] | v' @ V | 0.40462 |  |  |  |  | v' @ V | 0.15243 |  |  |  |  | v' @ V | -0.27179 |  |  |  |  | v' @ V | -0.85249 |  |  |  |  | v' @ V | 0.91322 |  |  |  |  | v' @ V | 0.88418 |  |  |  |  | v' @ V | 0.83536 |  |  |  |  | v' @ V | 0.75588 |  |  |  |  | v' @ V | 0.62979 |  |  |  |  | v' @ V | 0.41768 |  |  |  |  | v' @ V | 0.12733 |  |  |  |  | v' @ V | 1.0097 |  |  |  |  | v' @ V | 0.99946 |  |  |  |  | v' @ V | 0.98743 |  |  |  |  | v' @ V | 0.96186 |  |  |  |  | v' @ V | 0.91234 |  |  |  |  | v' @ V | 0.82332
| H Factor | 6.1299 | [5 empty] | H Factor | 6.3551 | [5 empty] | H Factor | 6.7457 | [5 empty] | H Factor | 7.3815 |  |  |  |  | H Factor | 8.3903 |  |  |  |  | H Factor | 10.0871 |  |  |  |  | H Factor | 12.41 |  |  |  |  | H Factor | 5.3471 |  |  |  |  | H Factor | 5.4633 |  |  |  |  | H Factor | 5.6586 |  |  |  |  | H Factor | 5.9765 |  |  |  |  | H Factor | 6.4809 |  |  |  |  | H Factor | 7.3293 |  |  |  |  | H Factor | 8.4907 |  |  |  |  | H Factor | 4.961 |  |  |  |  | H Factor | 5.0022 |  |  |  |  | H Factor | 5.0503 |  |  |  |  | H Factor | 5.1525 |  |  |  |  | H Factor | 5.3506 |  |  |  |  | H Factor | 5.7067
| R max != 2.7 | 6.4661 | 12.9321 |  |  |  |  | R max != 2.8 | 6.7357 | [5 empty] | R max != 2.9 | 7.296 | [5 empty] | R max != 2.10 | 8.6106 |  |  |  |  | R max != 2.11 | 14.029 |  |  |  |  | R max != 2.12 | #NUM! |  |  |  |  | R max != 2.13 | #NUM! |  |  |  |  | R max != 2.14 | 5.7316 |  |  |  |  | R max != 2.15 | 5.8249 |  |  |  |  | R max != 2.16 | 5.9927 |  |  |  |  | R max != 2.17 | 6.2999 |  |  |  |  | R max != 2.18 | 6.9018 |  |  |  |  | R max != 2.19 | 8.475 |  |  |  |  | R max != 2.20 | 15.3497 |  |  |  |  | R max != 2.21 | 5.4507 |  |  |  |  | R max != 2.22 | 5.4787 |  |  |  |  | R max != 2.23 | 5.512 |  |  |  |  | R max != 2.24 | 5.5847 |  |  |  |  | R max != 2.25 | 5.7343 |  |  |  |  | R max != 2.26 | 6.0364
| R_max_roomheight | 8.2753 | 16.5506 |  |  |  |  | R_max_roomheight | 8.5794 | [5 empty] | R_max_roomheight | 9.1067 | [5 empty] | R_max_roomheight | 9.965 |  |  |  |  | R_max_roomheight | 11.3269 |  |  |  |  | R_max_roomheight | 13.6177 |  |  |  |  | R_max_roomheight | 16.7534 |  |  |  |  | R_max_roomheight | 7.2186 |  |  |  |  | R_max_roomheight | 7.3754 |  |  |  |  | R_max_roomheight | 7.639 |  |  |  |  | R_max_roomheight | 8.0682 |  |  |  |  | R_max_roomheight | 8.7492 |  |  |  |  | R_max_roomheight | 9.8945 |  |  |  |  | R_max_roomheight | 11.4624 |  |  |  |  | R_max_roomheight | 6.6974 |  |  |  |  | R_max_roomheight | 6.7529 |  |  |  |  | R_max_roomheight | 6.8179 |  |  |  |  | R_max_roomheight | 6.9559 |  |  |  |  | R_max_roomheight | 7.2234 |  |  |  |  | R_max_roomheight | 7.7041
| R_max | 6.4661 | 12.9321 |  |  |  |  | R_max | 6.7357 | [5 empty] | R_max | 7.296 | [5 empty] | R_max | 8.6106 |  |  |  |  | R_max | 11.3269 |  |  |  |  | R_max | #NUM! |  |  |  |  | R_max | #NUM! |  |  |  |  | R_max | 5.7316 |  |  |  |  | R_max | 5.8249 |  |  |  |  | R_max | 5.9927 |  |  |  |  | R_max | 6.2999 |  |  |  |  | R_max | 6.9018 |  |  |  |  | R_max | 8.475 |  |  |  |  | R_max | 11.4624 |  |  |  |  | R_max | 5.4507 |  |  |  |  | R_max | 5.4787 |  |  |  |  | R_max | 5.512 |  |  |  |  | R_max | 5.5847 |  |  |  |  | R_max | 5.7343 |  |  |  |  | R_max | 6.0364
| Coverage max | 12.9321 | [5 empty] | Coverage max | 13.4715 | [5 empty] | Coverage max | 14.5919 | [5 empty] | Coverage max | 17.2212 |  |  |  |  | Coverage max | 22.6538 |  |  |  |  | Coverage max | #NUM! |  |  |  |  | Coverage max | #NUM! |  |  |  |  | Coverage max | 11.4631 |  |  |  |  | Coverage max | 11.6498 |  |  |  |  | Coverage max | 11.9854 |  |  |  |  | Coverage max | 12.5998 |  |  |  |  | Coverage max | 13.8037 |  |  |  |  | Coverage max | 16.95 |  |  |  |  | Coverage max | 22.9249 |  |  |  |  | Coverage max | 10.9015 |  |  |  |  | Coverage max | 10.9574 |  |  |  |  | Coverage max | 11.024 |  |  |  |  | Coverage max | 11.1695 |  |  |  |  | Coverage max | 11.4687 |  |  |  |  | Coverage max | 12.0727
| Centre Zone | [6 empty] | Centre Zone | [6 empty] | Centre Zone | [6 empty] | Centre Zone | [5 empty] | Centre Zone | [5 empty] | Centre Zone | [5 empty] | Centre Zone | [5 empty] | Centre Zone | [5 empty] | Centre Zone | [5 empty] | Centre Zone | [5 empty] | Centre Zone | [5 empty] | Centre Zone | [5 empty] | Centre Zone | [5 empty] | Centre Zone | [5 empty] | Centre Zone | [5 empty] | Centre Zone | [5 empty] | Centre Zone | [5 empty] | Centre Zone | [5 empty] | Centre Zone | [5 empty] | Centre Zone
| v' @ V | 0.58156 | [5 empty] | v' @ V | 0.53636 | [5 empty] | v' @ V | 0.45799 | [5 empty] | v' @ V | 0.33041 |  |  |  |  | v' @ V | 0.12799 |  |  |  |  | v' @ V | -0.2125 |  |  |  |  | v' @ V | -0.67859 |  |  |  |  | v' @ V | 0.73862 |  |  |  |  | v' @ V | 0.71532 |  |  |  |  | v' @ V | 0.67613 |  |  |  |  | v' @ V | 0.61234 |  |  |  |  | v' @ V | 0.51113 |  |  |  |  | v' @ V | 0.34089 |  |  |  |  | v' @ V | 0.10784 |  |  |  |  | v' @ V | 0.81609 |  |  |  |  | v' @ V | 0.80784 |  |  |  |  | v' @ V | 0.79819 |  |  |  |  | v' @ V | 0.77767 |  |  |  |  | v' @ V | 0.73791 |  |  |  |  | v' @ V | 0.66647
| H Factor | 6.1299 | [5 empty] | H Factor | 6.3551 | [5 empty] | H Factor | 6.7457 | [5 empty] | H Factor | 7.3815 |  |  |  |  | H Factor | 8.3903 |  |  |  |  | H Factor | 10.0871 |  |  |  |  | H Factor | 12.41 |  |  |  |  | H Factor | 5.3471 |  |  |  |  | H Factor | 5.4633 |  |  |  |  | H Factor | 5.6586 |  |  |  |  | H Factor | 5.9765 |  |  |  |  | H Factor | 6.4809 |  |  |  |  | H Factor | 7.3293 |  |  |  |  | H Factor | 8.4907 |  |  |  |  | H Factor | 4.961 |  |  |  |  | H Factor | 5.0022 |  |  |  |  | H Factor | 5.0503 |  |  |  |  | H Factor | 5.1525 |  |  |  |  | H Factor | 5.3506 |  |  |  |  | H Factor | 5.7067
| C_max!=2.7 | 14.3646 | [5 empty] | C_max!=2.8 | 14.9576 | [5 empty] | C_max!=2.9 | 16.1868 | [5 empty] | C_max!=2.10 | 19.0575 |  |  |  |  | C_max!=2.11 | 30.62 |  |  |  |  | C_max!=2.12 | #NUM! |  |  |  |  | C_max!=2.13 | #NUM! |  |  |  |  | C_max!=2.14 | 12.7462 |  |  |  |  | C_max!=2.15 | 12.9521 |  |  |  |  | C_max!=2.16 | 13.3222 |  |  |  |  | C_max!=2.17 | 13.9989 |  |  |  |  | C_max!=2.18 | 15.3223 |  |  |  |  | C_max!=2.19 | 18.7623 |  |  |  |  | C_max!=2.20 | 33.3578 |  |  |  |  | C_max!=2.21 | 12.1261 |  |  |  |  | C_max!=2.22 | 12.1879 |  |  |  |  | C_max!=2.23 | 12.2614 |  |  |  |  | C_max!=2.24 | 12.4221 |  |  |  |  | C_max!=2.25 | 12.7523 |  |  |  |  | C_max!=2.26 | 13.4184
| C_max_roomheight | 16.5506 | [5 empty] | C_max_roomheight | 17.1588 | [5 empty] | C_max_roomheight | 18.2133 | [5 empty] | C_max_roomheight | 19.9301 |  |  |  |  | C_max_roomheight | 22.6538 |  |  |  |  | C_max_roomheight | 27.2353 |  |  |  |  | C_max_roomheight | 33.5069 |  |  |  |  | C_max_roomheight | 14.4372 |  |  |  |  | C_max_roomheight | 14.7508 |  |  |  |  | C_max_roomheight | 15.2781 |  |  |  |  | C_max_roomheight | 16.1365 |  |  |  |  | C_max_roomheight | 17.4983 |  |  |  |  | C_max_roomheight | 19.7891 |  |  |  |  | C_max_roomheight | 22.9249 |  |  |  |  | C_max_roomheight | 13.3948 |  |  |  |  | C_max_roomheight | 13.5058 |  |  |  |  | C_max_roomheight | 13.6358 |  |  |  |  | C_max_roomheight | 13.9119 |  |  |  |  | C_max_roomheight | 14.4468 |  |  |  |  | C_max_roomheight | 15.4081
| C_max | 14.3646 | final selection |  |  |  |  | C_max | 14.9576 | final selection |  |  |  |  | C_max | 16.1868 | final selection |  |  |  |  | C_max | 19.0575 | final selection |  |  |  | C_max | 22.6538 | final selection |  |  |  | C_max | #NUM! | final selection |  |  |  | C_max | #NUM! | final selection |  |  |  | C_max | 12.7462 | final selection |  |  |  | C_max | 12.9521 | final selection |  |  |  | C_max | 13.3222 | final selection |  |  |  | C_max | 13.9989 | final selection |  |  |  | C_max | 15.3223 | final selection |  |  |  | C_max | 18.7623 | final selection |  |  |  | C_max | 22.9249 | final selection |  |  |  | C_max | 12.1261 | final selection |  |  |  | C_max | 12.1879 | final selection |  |  |  | C_max | 12.2614 | final selection |  |  |  | C_max | 12.4221 | final selection |  |  |  | C_max | 12.7523 | final selection |  |  |  | C_max | 13.4184 | final selection
| Coverage max - Centre Zone | [6 empty] | R max - Centre Zone | [6 empty] | R max - Centre Zone | [6 empty] | R max - Centre Zone | [5 empty] | R max - Centre Zone | [5 empty] | R max - Centre Zone | [5 empty] | R max - Centre Zone | [5 empty] | R max - Centre Zone | [5 empty] | R max - Centre Zone | [5 empty] | R max - Centre Zone | [5 empty] | R max - Centre Zone | [5 empty] | R max - Centre Zone | [5 empty] | R max - Centre Zone | [5 empty] | R max - Centre Zone | [5 empty] | R max - Centre Zone | [5 empty] | R max - Centre Zone | [5 empty] | R max - Centre Zone | [5 empty] | R max - Centre Zone | [5 empty] | R max - Centre Zone | [5 empty] | R max - Centre Zone
| v' @ V | 0.58156 | [5 empty] | v' @ V | 0.53636 | [5 empty] | v' @ V | 0.45799 | [5 empty] | v' @ V | 0.33041 |  |  |  |  | v' @ V | 0.12799 |  |  |  |  | v' @ V | -0.2125 |  |  |  |  | v' @ V | -0.67859 |  |  |  |  | v' @ V | 0.73862 |  |  |  |  | v' @ V | 0.71532 |  |  |  |  | v' @ V | 0.67613 |  |  |  |  | v' @ V | 0.61234 |  |  |  |  | v' @ V | 0.51113 |  |  |  |  | v' @ V | 0.34089 |  |  |  |  | v' @ V | 0.10784 |  |  |  |  | v' @ V | 0.81609 |  |  |  |  | v' @ V | 0.80784 |  |  |  |  | v' @ V | 0.79819 |  |  |  |  | v' @ V | 0.77767 |  |  |  |  | v' @ V | 0.73791 |  |  |  |  | v' @ V | 0.66647
| H factor | 6.1299 | [5 empty] | H factor | 6.3551 | [5 empty] | H factor | 6.7457 | [5 empty] | H factor | 7.3815 |  |  |  |  | H factor | 8.3903 |  |  |  |  | H factor | 10.0871 |  |  |  |  | H factor | 12.41 |  |  |  |  | H factor | 5.3471 |  |  |  |  | H factor | 5.4633 |  |  |  |  | H factor | 5.6586 |  |  |  |  | H factor | 5.9765 |  |  |  |  | H factor | 6.4809 |  |  |  |  | H factor | 7.3293 |  |  |  |  | H factor | 8.4907 |  |  |  |  | H factor | 4.961 |  |  |  |  | H factor | 5.0022 |  |  |  |  | H factor | 5.0503 |  |  |  |  | H factor | 5.1525 |  |  |  |  | H factor | 5.3506 |  |  |  |  | H factor | 5.7067
| R_max!=2.7 | 7.1823 | 14.3646 |  |  |  |  | R_max!=2.8 | 7.4788 | [5 empty] | R_max!=2.9 | 8.0934 | [5 empty] | R_max!=2.10 | 9.5287 |  |  |  |  | R_max!=2.11 | 15.31 |  |  |  |  | R_max!=2.12 | #NUM! |  |  |  |  | R_max!=2.13 | #NUM! |  |  |  |  | R_max!=2.14 | 6.3731 |  |  |  |  | R_max!=2.15 | 6.4761 |  |  |  |  | R_max!=2.16 | 6.6611 |  |  |  |  | R_max!=2.17 | 6.9995 |  |  |  |  | R_max!=2.18 | 7.6612 |  |  |  |  | R_max!=2.19 | 9.3812 |  |  |  |  | R_max!=2.20 | 16.6789 |  |  |  |  | R_max!=2.21 | 6.063 |  |  |  |  | R_max!=2.22 | 6.0939 |  |  |  |  | R_max!=2.23 | 6.1307 |  |  |  |  | R_max!=2.24 | 6.211 |  |  |  |  | R_max!=2.25 | 6.3761 |  |  |  |  | R_max!=2.26 | 6.7092
| R_max_roomheight | 8.2753 | 16.5506 |  |  |  |  | R_max_roomheight | 8.5794 | [5 empty] | R_max_roomheight | 9.1067 | [5 empty] | R_max_roomheight | 9.965 |  |  |  |  | R_max_roomheight | 11.3269 |  |  |  |  | R_max_roomheight | 13.6177 |  |  |  |  | R_max_roomheight | 16.7534 |  |  |  |  | R_max_roomheight | 7.2186 |  |  |  |  | R_max_roomheight | 7.3754 |  |  |  |  | R_max_roomheight | 7.639 |  |  |  |  | R_max_roomheight | 8.0682 |  |  |  |  | R_max_roomheight | 8.7492 |  |  |  |  | R_max_roomheight | 9.8945 |  |  |  |  | R_max_roomheight | 11.4624 |  |  |  |  | R_max_roomheight | 6.6974 |  |  |  |  | R_max_roomheight | 6.7529 |  |  |  |  | R_max_roomheight | 6.8179 |  |  |  |  | R_max_roomheight | 6.9559 |  |  |  |  | R_max_roomheight | 7.2234 |  |  |  |  | R_max_roomheight | 7.7041
| R_max | 7.1823 | 14.3646 |  |  |  |  | R_max | 7.4788 | [5 empty] | R_max | 8.0934 | [5 empty] | R_max | 9.5287 |  |  |  |  | R_max | 11.3269 |  |  |  |  | R_max | #NUM! |  |  |  |  | R_max | #NUM! |  |  |  |  | R_max | 6.3731 |  |  |  |  | R_max | 6.4761 |  |  |  |  | R_max | 6.6611 |  |  |  |  | R_max | 6.9995 |  |  |  |  | R_max | 7.6612 |  |  |  |  | R_max | 9.3812 |  |  |  |  | R_max | 11.4624 |  |  |  |  | R_max | 6.063 |  |  |  |  | R_max | 6.0939 |  |  |  |  | R_max | 6.1307 |  |  |  |  | R_max | 6.211 |  |  |  |  | R_max | 6.3761 |  |  |  |  | R_max | 6.7092
| Coverage max | 14.3646 | [5 empty] | Coverage max | 14.9576 | [5 empty] | Coverage max | 16.1868 | [5 empty] | Coverage max | 19.0575 |  |  |  |  | Coverage max | 22.6538 |  |  |  |  | Coverage max | #NUM! |  |  |  |  | Coverage max | #NUM! |  |  |  |  | Coverage max | 12.7462 |  |  |  |  | Coverage max | 12.9521 |  |  |  |  | Coverage max | 13.3222 |  |  |  |  | Coverage max | 13.9989 |  |  |  |  | Coverage max | 15.3223 |  |  |  |  | Coverage max | 18.7623 |  |  |  |  | Coverage max | 22.9249 |  |  |  |  | Coverage max | 12.1261 |  |  |  |  | Coverage max | 12.1879 |  |  |  |  | Coverage max | 12.2614 |  |  |  |  | Coverage max | 12.4221 |  |  |  |  | Coverage max | 12.7523 |  |  |  |  | Coverage max | 13.4184
| Heating | [6 empty] | Heating | [6 empty] | Heating | [6 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating
| heatingX | 8.5112 |  | -0.000142 | 0.0948 | -0.82 |  | heatingX | 9.0028 |  | -0.000173 | 0.104 | -0.986 |  | heatingX | 9.5584 |  | -0.0001404 | 0.1011 | -0.5518 |  | heatingX | 10.597 |  | -0.0002262 | 0.1219 | -0.7737 | heatingX | 11.4306 |  | -0.0004085 | 0.1533 | -1.083 | heatingX | 12.8051 |  | -0.0003648 | 0.1573 | -0.8178 | heatingX | 13.768 |  | -0.0005475 | 0.189 | -1.028 | heatingX | 6.1499 |  | -6.82e-05 | 0.0668 | -0.884 | heatingX | 6.4978 |  | -8.14e-05 | 0.0722 | -0.994 | heatingX | 7.2292 |  | -0.000142 | 0.0882 | -1.31 | heatingX | 8.023 |  | -0.000115 | 0.0873 | -0.797 | heatingX | 9.0028 |  | -0.000173 | 0.104 | -0.986 | heatingX | 9.9726 |  | -0.000201 | 0.114 | -0.813 | heatingX | 11.1586 |  | -0.000256 | 0.13 | -0.755 | heatingX | 4.5622 |  | -1.7e-05 | 0.0377 | 0.283 | heatingX | 4.885 |  | -2.66e-05 | 0.0457 | -0.216 | heatingX | 5.3586 |  | -3.19e-05 | 0.0499 | -0.17 | heatingX | 5.8283 |  | -3.63e-05 | 0.0536 | -0.081 | heatingX | 6.2876 |  | -3.91e-05 | 0.0564 | 0.0826 | heatingX | 6.6744 |  | -4.15e-05 | 0.0594 | 0.144
| heatingSlope | 0.67328 |  | 0.0656 | -0.7582 | 2.2422 |  | heatingSlope | 0.67328 |  | 0.0656 | -0.7582 | 2.2422 |  | heatingSlope | 0.67328 |  | 0.0656 | -0.7582 | 2.2422 |  | heatingSlope | 0.67328 |  | 0.0656 | -0.7582 | 2.2422 | heatingSlope | 0.67328 |  | 0.0656 | -0.7582 | 2.2422 | heatingSlope | 0.67328 |  | 0.0656 | -0.7582 | 2.2422 | heatingSlope | 0.67328 |  | 0.0656 | -0.7582 | 2.2422 | heatingSlope | 0.67328 |  | 0.0656 | -0.7582 | 2.2422 | heatingSlope | 0.67328 |  | 0.0656 | -0.7582 | 2.2422 | heatingSlope | 0.67328 |  | 0.0656 | -0.7582 | 2.2422 | heatingSlope | 0.67328 |  | 0.0656 | -0.7582 | 2.2422 | heatingSlope | 0.67328 |  | 0.0656 | -0.7582 | 2.2422 | heatingSlope | 0.67328 |  | 0.0656 | -0.7582 | 2.2422 | heatingSlope | 0.67328 |  | 0.0656 | -0.7582 | 2.2422 | heatingSlope | 0.67486 |  | 0.0746 | -0.8311 | 2.375 | heatingSlope | 0.67486 |  | 0.0746 | -0.8311 | 2.375 | heatingSlope | 0.67486 |  | 0.0746 | -0.8311 | 2.375 | heatingSlope | 0.67486 |  | 0.0746 | -0.8311 | 2.375 | heatingSlope | 0.67486 |  | 0.0746 | -0.8311 | 2.375 | heatingSlope | 0.67486 |  | 0.0746 | -0.8311 | 2.375
| heatingY | 5.7305 | [5 empty] | heatingY | 6.0614 | [5 empty] | heatingY | 6.4355 | [5 empty] | heatingY | 7.1348 |  |  |  |  | heatingY | 7.696 |  |  |  |  | heatingY | 8.6215 |  |  |  |  | heatingY | 9.2698 |  |  |  |  | heatingY | 4.1406 |  |  |  |  | heatingY | 4.3749 |  |  |  |  | heatingY | 4.8673 |  |  |  |  | heatingY | 5.4018 |  |  |  |  | heatingY | 6.0614 |  |  |  |  | heatingY | 6.7144 |  |  |  |  | heatingY | 7.5129 |  |  |  |  | heatingY | 3.0789 |  |  |  |  | heatingY | 3.2967 |  |  |  |  | heatingY | 3.6164 |  |  |  |  | heatingY | 3.9333 |  |  |  |  | heatingY | 4.2432 |  |  |  |  | heatingY | 4.5043
| dT_10L/s | 12.7216 |  |  | 2.22 | 0 |  | dT_10L/s | 13.4564 |  |  | 2.22 | 0 |  | dT_10L/s | 14.2869 |  |  | 2.22 | 0 |  | dT_10L/s | 15.8393 |  |  | 2.22 | 0 | dT_10L/s | 17.0852 |  |  | 2.22 | 0 | dT_10L/s | 19.1396 |  |  | 2.22 | 0 | dT_10L/s | 20.5789 |  |  | 2.22 | 0 | dT_10L/s | 9.1922 |  |  | 2.22 | 0 | dT_10L/s | 9.7123 |  |  | 2.22 | 0 | dT_10L/s | 10.8054 |  |  | 2.22 | 0 | dT_10L/s | 11.9919 |  |  | 2.22 | 0 | dT_10L/s | 13.4564 |  |  | 2.22 | 0 | dT_10L/s | 14.906 |  |  | 2.22 | 0 | dT_10L/s | 16.6787 |  |  | 2.22 | 0 | dT_10L/s | 6.8351 |  |  | 2.22 | 0 | dT_10L/s | 7.3186 |  |  | 2.22 | 0 | dT_10L/s | 8.0283 |  |  | 2.22 | 0 | dT_10L/s | 8.7319 |  |  | 2.22 | 0 | dT_10L/s | 9.42 |  |  | 2.22 | 0 | dT_10L/s | 9.9996 |  |  | 2.22 | 0
| specVfactor | 0.70353 |  | -0.00506 | 0.101 | 0.498 |  | specVfactor | 0.70353 |  | -0.00506 | 0.101 | 0.498 |  | specVfactor | 0.70353 |  | -0.00506 | 0.101 | 0.498 |  | specVfactor | 0.70353 |  | -0.00506 | 0.101 | 0.498 | specVfactor | 0.70353 |  | -0.00506 | 0.101 | 0.498 | specVfactor | 0.70353 |  | -0.00506 | 0.101 | 0.498 | specVfactor | 0.70353 |  | -0.00506 | 0.101 | 0.498 | specVfactor | 0.70353 |  | -0.00506 | 0.101 | 0.498 | specVfactor | 0.70353 |  | -0.00506 | 0.101 | 0.498 | specVfactor | 0.70353 |  | -0.00506 | 0.101 | 0.498 | specVfactor | 0.70353 |  | -0.00506 | 0.101 | 0.498 | specVfactor | 0.70353 |  | -0.00506 | 0.101 | 0.498 | specVfactor | 0.70353 |  | -0.00506 | 0.101 | 0.498 | specVfactor | 0.70353 |  | -0.00506 | 0.101 | 0.498 | specVfactor | 0.70353 |  | -0.00506 | 0.101 | 0.498 | specVfactor | 0.70353 |  | -0.00506 | 0.101 | 0.498 | specVfactor | 0.70353 |  | -0.00506 | 0.101 | 0.498 | specVfactor | 0.70353 |  | -0.00506 | 0.101 | 0.498 | specVfactor | 0.70353 |  | -0.00506 | 0.101 | 0.498 | specVfactor | 0.70353 |  | -0.00506 | 0.101 | 0.498
| dT_heating | 8.9501 | [5 empty] | dT_heating | 9.467 | [5 empty] | dT_heating | 10.0513 | [5 empty] | dT_heating | 11.1434 |  |  |  |  | dT_heating | 12.02 |  |  |  |  | dT_heating | 13.4654 |  |  |  |  | dT_heating | 14.4779 |  |  |  |  | dT_heating | 6.467 |  |  |  |  | dT_heating | 6.8329 |  |  |  |  | dT_heating | 7.602 |  |  |  |  | dT_heating | 8.4367 |  |  |  |  | dT_heating | 9.467 |  |  |  |  | dT_heating | 10.4868 |  |  |  |  | dT_heating | 11.734 |  |  |  |  | dT_heating | 4.8087 |  |  |  |  | dT_heating | 5.1489 |  |  |  |  | dT_heating | 5.6482 |  |  |  |  | dT_heating | 6.1432 |  |  |  |  | dT_heating | 6.6273 |  |  |  |  | dT_heating | 7.035
| dT_heating Centre | 13.4251 | [5 empty] | dT_heating Centre | 14.2005 | [5 empty] | dT_heating Centre | 15.077 | [5 empty] | dT_heating Centre | 16.7152 |  |  |  |  | dT_heating Centre | 18.03 |  |  |  |  | dT_heating Centre | 20.198 |  |  |  |  | dT_heating Centre | 21.7169 |  |  |  |  | dT_heating Centre | 9.7005 |  |  |  |  | dT_heating Centre | 10.2493 |  |  |  |  | dT_heating Centre | 11.4029 |  |  |  |  | dT_heating Centre | 12.655 |  |  |  |  | dT_heating Centre | 14.2005 |  |  |  |  | dT_heating Centre | 15.7302 |  |  |  |  | dT_heating Centre | 17.601 |  |  |  |  | dT_heating Centre | 7.2131 |  |  |  |  | dT_heating Centre | 7.7234 |  |  |  |  | dT_heating Centre | 8.4723 |  |  |  |  | dT_heating Centre | 9.2148 |  |  |  |  | dT_heating Centre | 9.9409 |  |  |  |  | dT_heating Centre | 10.5525
| DR | [6 empty] | DR | [6 empty] | DR | [6 empty] | DR | [5 empty] | DR | [5 empty] | DR | [5 empty] | DR | [5 empty] | DR | [5 empty] | DR | [5 empty] | DR | [5 empty] | DR | [5 empty] | DR | [5 empty] | DR | [5 empty] | DR | [5 empty] | DR | [5 empty] | DR | [5 empty] | DR | [5 empty] | DR | [5 empty] | DR | [5 empty] | DR
| velocity adjustment | [6 empty] | velocity adjustment | [6 empty] | velocity adjustment | [6 empty] | velocity adjustment | [5 empty] | velocity adjustment | [5 empty] | velocity adjustment | [5 empty] | velocity adjustment | [5 empty] | velocity adjustment | [5 empty] | velocity adjustment | [5 empty] | velocity adjustment | [5 empty] | velocity adjustment | [5 empty] | velocity adjustment | [5 empty] | velocity adjustment | [5 empty] | velocity adjustment | [5 empty] | velocity adjustment | [5 empty] | velocity adjustment | [5 empty] | velocity adjustment | [5 empty] | velocity adjustment | [5 empty] | velocity adjustment | [5 empty] | velocity adjustment
| v'' correction factor | -0.074675 |  | Note: density of air ignored to compensate for mean velocity from max velocity |  |  |  | v'' correction factor | -0.20418 | [5 empty] | v'' correction factor | -0.42876 | [5 empty] | v'' correction factor | -0.79436 |  |  |  |  | v'' correction factor | -1.3744 |  |  |  |  | v'' correction factor | -2.3501 |  |  |  |  | v'' correction factor | -3.6857 |  |  |  |  | v'' correction factor | 0.3754 |  |  |  |  | v'' correction factor | 0.30862 |  |  |  |  | v'' correction factor | 0.19633 |  |  |  |  | v'' correction factor | 0.013532 |  |  |  |  | v'' correction factor | -0.27649 |  |  |  |  | v'' correction factor | -0.76434 |  |  |  |  | v'' correction factor | -1.4321 |  |  |  |  | v'' correction factor | 0.5974 |  |  |  |  | v'' correction factor | 0.57376 |  |  |  |  | v'' correction factor | 0.54609 |  |  |  |  | v'' correction factor | 0.48729 |  |  |  |  | v'' correction factor | 0.37338 |  |  |  |  | v'' correction factor | 0.16864 |  |  |  |  | v'' correction factor
| v'' (adjusted) | 2.3747 | [5 empty] | v'' (adjusted) | 2.5042 | [5 empty] | v'' (adjusted) | 2.7288 | [5 empty] | v'' (adjusted) | 3.0944 |  |  |  |  | v'' (adjusted) | 3.6744 |  |  |  |  | v'' (adjusted) | 4.6501 |  |  |  |  | v'' (adjusted) | 5.9857 |  |  |  |  | v'' (adjusted) | 1.9246 |  |  |  |  | v'' (adjusted) | 1.9914 |  |  |  |  | v'' (adjusted) | 2.1037 |  |  |  |  | v'' (adjusted) | 2.2865 |  |  |  |  | v'' (adjusted) | 2.5765 |  |  |  |  | v'' (adjusted) | 3.0643 |  |  |  |  | v'' (adjusted) | 3.7321 |  |  |  |  | v'' (adjusted) | 1.7026 |  |  |  |  | v'' (adjusted) | 1.7262 |  |  |  |  | v'' (adjusted) | 1.7539 |  |  |  |  | v'' (adjusted) | 1.8127 |  |  |  |  | v'' (adjusted) | 1.9266 |  |  |  |  | v'' (adjusted) | 2.1314
| Q'' (adjusted) | 28.4961 | [5 empty] | Q'' (adjusted) | 30.0502 | [5 empty] | Q'' (adjusted) | 32.7452 | [5 empty] | Q'' (adjusted) | 37.1324 |  |  |  |  | Q'' (adjusted) | 44.093 |  |  |  |  | Q'' (adjusted) | 55.8013 |  |  |  |  | Q'' (adjusted) | 71.8287 |  |  |  |  | Q'' (adjusted) | 23.0952 |  |  |  |  | Q'' (adjusted) | 23.8965 |  |  |  |  | Q'' (adjusted) | 25.244 |  |  |  |  | Q'' (adjusted) | 27.4376 |  |  |  |  | Q'' (adjusted) | 30.9179 |  |  |  |  | Q'' (adjusted) | 36.7721 |  |  |  |  | Q'' (adjusted) | 44.7858 |  |  |  |  | Q'' (adjusted) | 20.4312 |  |  |  |  | Q'' (adjusted) | 20.7149 |  |  |  |  | Q'' (adjusted) | 21.0469 |  |  |  |  | Q'' (adjusted) | 21.7525 |  |  |  |  | Q'' (adjusted) | 23.1195 |  |  |  |  | Q'' (adjusted) | 25.5763
| 2.7 | 0.02455 | 0.4405 | 0.10737 |  |  |  | 2.7 | 0.0246 | 0.441 | 0.11032 |  |  |  | 2.7 | 0.0246 | 0.441 | 0.11458 |  |  |  | 2.7 | 0.0246 | 0.441 | 0.12111 |  |  | 2.7 | 0.0246 | 0.441 | 0.13065 |  |  | 2.7 | 0.0246 | 0.441 | 0.14495 |  |  | 2.7 | 0.0246 | 0.441 | 0.16202 |  |  | 2.7 | 0.02455 | 0.4405 | 0.097877 |  |  | 2.7 | 0.02455 | 0.4405 | 0.099359 |  |  | 2.7 | 0.02455 | 0.4405 | 0.10179 |  |  | 2.7 | 0.02455 | 0.4405 | 0.10559 |  |  | 2.7 | 0.02455 | 0.4405 | 0.1113 |  |  | 2.7 | 0.02455 | 0.4405 | 0.12013 |  |  | 2.7 | 0.02455 | 0.4405 | 0.13103 |  |  | 2.7 | 0.02455 | 0.4405 | 0.092733 |  |  | 2.7 | 0.02455 | 0.4405 | 0.093298 |  |  | 2.7 | 0.02455 | 0.4405 | 0.093954 |  |  | 2.7 | 0.02455 | 0.4405 | 0.095329 |  |  | 2.7 | 0.02455 | 0.4405 | 0.097923 |  |  | 2.7 | 0.02455 | 0.4405 | 0.10238
| 4 | 0.0251 | 0.4458 | 0.11174 |  |  |  | 4 | 0.0251 | 0.446 | 0.1145 |  |  |  | 4 | 0.0251 | 0.446 | 0.11897 |  |  |  | 4 | 0.0251 | 0.446 | 0.12583 |  |  | 4 | 0.0251 | 0.446 | 0.13585 |  |  | 4 | 0.0251 | 0.446 | 0.1509 |  |  | 4 | 0.0251 | 0.446 | 0.16888 |  |  | 4 | 0.0251 | 0.4458 | 0.10175 |  |  | 4 | 0.0251 | 0.4458 | 0.10331 |  |  | 4 | 0.0251 | 0.4458 | 0.10587 |  |  | 4 | 0.0251 | 0.4458 | 0.10987 |  |  | 4 | 0.0251 | 0.4458 | 0.11588 |  |  | 4 | 0.0251 | 0.4458 | 0.12519 |  |  | 4 | 0.0251 | 0.4458 | 0.13669 |  |  | 4 | 0.0251 | 0.4458 | 0.096339 |  |  | 4 | 0.0251 | 0.4458 | 0.096933 |  |  | 4 | 0.0251 | 0.4458 | 0.097623 |  |  | 4 | 0.0251 | 0.4458 | 0.099069 |  |  | 4 | 0.0251 | 0.4458 | 0.1018 |  |  | 4 | 0.0251 | 0.4458 | 0.10648
| 10 | 0.02797 | 0.4391 | 0.12176 |  |  |  | 10 | 0.028 | 0.439 | 0.12472 |  |  |  | 10 | 0.028 | 0.439 | 0.12951 |  |  |  | 10 | 0.028 | 0.439 | 0.13686 |  |  | 10 | 0.028 | 0.439 | 0.14758 |  |  | 10 | 0.028 | 0.439 | 0.16366 |  |  | 10 | 0.028 | 0.439 | 0.18284 |  |  | 10 | 0.02797 | 0.4391 | 0.11102 |  |  | 10 | 0.02797 | 0.4391 | 0.1127 |  |  | 10 | 0.02797 | 0.4391 | 0.11545 |  |  | 10 | 0.02797 | 0.4391 | 0.11975 |  |  | 10 | 0.02797 | 0.4391 | 0.1262 |  |  | 10 | 0.02797 | 0.4391 | 0.13618 |  |  | 10 | 0.02797 | 0.4391 | 0.14849 |  |  | 10 | 0.02797 | 0.4391 | 0.10521 |  |  | 10 | 0.02797 | 0.4391 | 0.10585 |  |  | 10 | 0.02797 | 0.4391 | 0.10659 |  |  | 10 | 0.02797 | 0.4391 | 0.10814 |  |  | 10 | 0.02797 | 0.4391 | 0.11107 |  |  | 10 | 0.02797 | 0.4391 | 0.11611
| Room height | Ax | ^b |  |  |  |  | Room height | Ax | ^b |  |  |  |  | Room height | Ax | ^b |  |  |  |  | Room height | Ax | ^b |  |  |  | Room height | Ax | ^b |  |  |  | Room height | Ax | ^b |  |  |  | Room height | Ax | ^b |  |  |  | Room height | Ax | ^b |  |  |  | Room height | Ax | ^b |  |  |  | Room height | Ax | ^b |  |  |  | Room height | Ax | ^b |  |  |  | Room height | Ax | ^b |  |  |  | Room height | Ax | ^b |  |  |  | Room height | Ax | ^b |  |  |  | Room height | Ax | ^b |  |  |  | Room height | Ax | ^b |  |  |  | Room height | Ax | ^b |  |  |  | Room height | Ax | ^b |  |  |  | Room height | Ax | ^b |  |  |  | Room height | Ax | ^b
| 2.7 | 0.097737 | 0.095608 | 0.10747 | m/s |  |  | 2.7 | 0.10054 | 0.093614 | 0.11034 | m/s |  |  | 2.7 | 0.10447 | 0.09339 | 0.11462 | m/s |  |  | 2.7 | 0.11049 | 0.093062 | 0.1212 | m/s |  | 2.7 | 0.1193 | 0.092614 | 0.13079 | m/s |  | 2.7 | 0.13251 | 0.091999 | 0.14519 | m/s |  | 2.7 | 0.14831 | 0.09134 | 0.16239 | m/s |  | 2.7 | 0.089008 | 0.096065 | 0.097919 | m/s |  | 2.7 | 0.09037 | 0.095991 | 0.09941 | m/s |  | 2.7 | 0.092604 | 0.095872 | 0.10186 | m/s |  | 2.7 | 0.096104 | 0.09569 | 0.10569 | m/s |  | 2.7 | 0.10135 | 0.095431 | 0.11143 | m/s |  | 2.7 | 0.10949 | 0.095054 | 0.12033 | m/s |  | 2.7 | 0.11953 | 0.094625 | 0.13131 | m/s |  | 2.7 | 0.084282 | 0.096331 | 0.092744 | m/s |  | 2.7 | 0.084801 | 0.096301 | 0.093312 | m/s |  | 2.7 | 0.085403 | 0.096267 | 0.093972 | m/s |  | 2.7 | 0.086666 | 0.096195 | 0.095355 | m/s |  | 2.7 | 0.08905 | 0.096063 | 0.097965 | m/s |  | 2.7 | 0.093145 | 0.095843 | 0.10245 | m/s
| Velocity | 0.10747 | [5 empty] | Velocity | 0.11034 | [5 empty] | Velocity | 0.11462 | [5 empty] | Velocity | 0.1212 |  |  |  |  | Velocity | 0.13079 |  |  |  |  | Velocity | 0.14519 |  |  |  |  | Velocity | 0.16239 |  |  |  |  | Velocity | 0.097919 |  |  |  |  | Velocity | 0.09941 |  |  |  |  | Velocity | 0.10186 |  |  |  |  | Velocity | 0.10569 |  |  |  |  | Velocity | 0.11143 |  |  |  |  | Velocity | 0.12033 |  |  |  |  | Velocity | 0.13131 |  |  |  |  | Velocity | 0.092744 |  |  |  |  | Velocity | 0.093312 |  |  |  |  | Velocity | 0.093972 |  |  |  |  | Velocity | 0.095355 |  |  |  |  | Velocity | 0.097965 |  |  |  |  | Velocity | 0.10245
| Draught Rating | 8.855% | [5 empty] | Draught Rating | 9.208% | [5 empty] | Draught Rating | 9.735% | [5 empty] | Draught Rating | 10.55% |  |  |  |  | Draught Rating | 11.73% |  |  |  |  | Draught Rating | 13.54% |  |  |  |  | Draught Rating | 15.73% |  |  |  |  | Draught Rating | 7.674% |  |  |  |  | Draught Rating | 7.859% |  |  |  |  | Draught Rating | 8.162% |  |  |  |  | Draught Rating | 8.635% |  |  |  |  | Draught Rating | 9.342% |  |  |  |  | Draught Rating | 10.44% |  |  |  |  | Draught Rating | 11.8% |  |  |  |  | Draught Rating | 7.03% |  |  |  |  | Draught Rating | 7.101% |  |  |  |  | Draught Rating | 7.184% |  |  |  |  | Draught Rating | 7.356% |  |  |  |  | Draught Rating | 7.68% |  |  |  |  | Draught Rating | 8.235%
| PPD | 5.606% | [5 empty] | PPD | 5.726% | [5 empty] | PPD | 5.908% | [5 empty] | PPD | 6.193% |  |  |  |  | PPD | 6.622% |  |  |  |  | PPD | 7.3% |  |  |  |  | PPD | 8.168% |  |  |  |  | PPD | 5.213% |  |  |  |  | PPD | 5.274% |  |  |  |  | PPD | 5.374% |  |  |  |  | PPD | 5.531% |  |  |  |  | PPD | 5.772% |  |  |  |  | PPD | 6.154% |  |  |  |  | PPD | 6.646% |  |  |  |  | PPD | 5.005% |  |  |  |  | PPD | 5.027% |  |  |  |  | PPD | 5.054% |  |  |  |  | PPD | 5.11% |  |  |  |  | PPD | 5.215% |  |  |  |  | PPD | 5.398%
| PPD class | A | [5 empty] | PPD class | A | [5 empty] | PPD class | A | [5 empty] | PPD class | B |  |  |  |  | PPD class | B |  |  |  |  | PPD class | B |  |  |  |  | PPD class | B |  |  |  |  | PPD class | A |  |  |  |  | PPD class | A |  |  |  |  | PPD class | A |  |  |  |  | PPD class | A |  |  |  |  | PPD class | A |  |  |  |  | PPD class | B |  |  |  |  | PPD class | B |  |  |  |  | PPD class | A |  |  |  |  | PPD class | A |  |  |  |  | PPD class | A |  |  |  |  | PPD class | A |  |  |  |  | PPD class | A |  |  |  |  | PPD class | A
| PMV | 0.14126 | [5 empty] | PMV | 0.15895 | [5 empty] | PMV | 0.18418 | [5 empty] | PMV | 0.22038 |  |  |  |  | PMV | 0.26872 |  |  |  |  | PMV | 0.33336 |  |  |  |  | PMV | 0.40127 |  |  |  |  | PMV | 0.076494 |  |  |  |  | PMV | 0.087266 |  |  |  |  | PMV | 0.10436 |  |  |  |  | PMV | 0.12986 |  |  |  |  | PMV | 0.16551 |  |  |  |  | PMV | 0.21575 |  |  |  |  | PMV | 0.27119 |  |  |  |  | PMV | 0.036798 |  |  |  |  | PMV | 0.041349 |  |  |  |  | PMV | 0.046569 |  |  |  |  | PMV | 0.0573 |  |  |  |  | PMV | 0.076828 |  |  |  |  | PMV | 0.1084
| PMV | 0.2 | [5 empty] | PMV | 0.2 | [5 empty] | PMV | 0.2 | [5 empty] | PMV | 0.2 |  |  |  |  | PMV | 0.3 |  |  |  |  | PMV | 0.3 |  |  |  |  | PMV | 0.4 | [5 empty] | 0.2 | [5 empty] | 0.2 | [5 empty] | 0.2 | [5 empty] | 0.2 | [5 empty] | 0.2 | [5 empty] | 0.2 | [5 empty] | 0.3 | [5 empty] | 0.2 | [5 empty] | 0.2 | [5 empty] | 0.2 | [5 empty] | 0.2 | [5 empty] | 0.2 | [5 empty] | 0.2
| Global Distances | 0 | 1 | 2 | 3 | 4 | 5 | 6
| Cmax | 11.5 | 11.6 | 12 | 12.6 | 13.8 | 17 | 22.9
| Cmin | 2.5 | 2.6 | 2.6 | 2.7 | 2.9 | 3.4 | 4.5
| Gray Column | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE
| Cmax | 0.2 0: 11.5; 0.2 1: 11.6; 0.2 2: 12; 0.2 3: 12.6
| Cmin | 0.2 0: 2.5; 0.2 1: 2.6; 0.2 2: 2.6; 0.2 3: 2.7
| Total Avg | 0.2 0: 7.2625
| Case 1 Avg v'' | 0.2 0: 2.2751
| Case 2 v'' | 0.2 0: 1.875
| Specified Specific Flowrate | 0.2 0: 15
| V'' | 0.2 0: 2.3
| v" unit converted for display | 0.2 0: 2.3
| V'' for heating | 0.2 0: 2.3
| C Selected | 0.2 0: 7.3
| max spec fr | 0.2 0: 30
Collated Results
|  | 0.2 0: DN250 | DN355 | [6 empty] | DN500 | [5 empty] | DN500 Empty
|  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 0 | 1 | 2 | 3 | 4 | 5
| Max Airflow | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
| Max Recommended Airflow | 115.1488 | 102.1226 | 87.0697 | 64.6133 | 48.4867 | 32.2037 | 22.8365 | 239.9098 | 204.2451 | 174.1395 | 129.2267 | 96.9735 | 64.4075 | 45.6731 | 506.6228 | 444.9775 | 391.276 | 325.2069 | 238.8243 | 165.3178
| Min Airflow | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
| Min Permissible Airflow | 23.8157 | 20.8084 | 17.0704 | 13.208 | 9.719 | 6.729 | 4.735 | 47.8479 | 41.6169 | 34.1409 | 26.4159 | 19.4379 | 13.458 | 9.47 | 95.2628 | 86.1695 | 77.5093 | 63.8694 | 47.6314 | 32.6925
| Min % TD to | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Min Permissible % Turndown to | 19.85% | 17.34% | 14.23% | 11.01% | 8.099% | 5.608% | 3.946% | 0.39873 | 0.34681 | 0.28451 | 0.22013 | 0.16198 | 0.11215 | 0.078917 | 0.79386 | 0.71808 | 0.64591 | 0.53224 | 0.39693 | 0.27244
| Static Pressure | 38.0112 | 48.3267 | 66.4808 | 120.7219 | 214.3801 | 485.9796 | 966.429 | 8.7566 | 12.0817 | 16.6202 | 30.1805 | 53.595 | 121.4949 | 241.6073 | 1.9636 | 2.5454 | 3.292 | 4.7655 | 8.8364 | 18.4413
| Total Pressure | 41.6549 | 51.9703 | 70.1244 | 124.3656 | 218.0238 | 489.6233 | 970.0727 | 12.4002 | 15.7253 | 20.2638 | 33.8241 | 57.2387 | 125.1386 | 245.2509 | 5.6073 | 6.189 | 6.9357 | 8.4092 | 12.48 | 22.0849
| Max Permissible P | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
| Sound Power Level | 44.6244 | 47.3244 | 50.849 | 57.5503 | 64.0005 | 73.1884 | 80.9009 | 27.2367 | 31.9502 | 37.0186 | 40.754 | 46.0134 | 54.0008 | 60.136 | 8.3727 | 11.3006 | 22.1738 | 24.1202 | 27.8611 | 33.809
| Sound Pressure Level | 29.6244 | 32.3244 | 35.849 | 42.5503 | 49.0005 | 58.1884 | 65.9009 | 12.2367 | 16.9502 | 22.0186 | 25.754 | 31.0134 | 39.0008 | 45.136 | -6.6273 | -3.6994 | 7.1738 | 9.1202 | 12.8611 | 18.809
| ΔT_max centre | 13.4251 | 14.2005 | 15.077 | 16.7152 | 18.03 | 20.198 | 21.7169 | 9.7005 | 10.2493 | 11.4029 | 12.655 | 14.2005 | 15.7302 | 17.601 | 7.2131 | 7.7234 | 8.4723 | 9.2148 | 9.9409 | 10.5525
| ΔT_max (heating) | 8.9501 | 9.467 | 10.0513 | 11.1434 | 12.02 | 13.4654 | 14.4779 | 6.467 | 6.8329 | 7.602 | 8.4367 | 9.467 | 10.4868 | 11.734 | 4.8087 | 5.1489 | 5.6482 | 6.1432 | 6.6273 | 7.035
| Cmax (centre) | 14.3646 | 14.9576 | 16.1868 | 19.0575 | 22.6538 | #NUM! | #NUM! | 12.7462 | 12.9521 | 13.3222 | 13.9989 | 15.3223 | 18.7623 | 22.9249 | 12.1261 | 12.1879 | 12.2614 | 12.4221 | 12.7523 | 13.4184
| Cmax (perimeter) | 12.9321 | 13.4715 | 14.5919 | 17.2212 | 22.6538 | #NUM! | #NUM! | 11.4631 | 11.6498 | 11.9854 | 12.5998 | 13.8037 | 16.95 | 22.9249 | 10.9015 | 10.9574 | 11.024 | 11.1695 | 11.4687 | 12.0727
| Cmin | 2.7868 | 2.8718 | 3.0396 | 3.3895 | 4.3269 | #VALUE! | #VALUE! | 2.5412 | 2.5736 | 2.6309 | 2.7331 | 2.9228 | 3.3562 | 4.4692 | 2.4418 | 2.4518 | 2.4637 | 2.4896 | 2.5422 | 2.6457
| Hmin | 2.2723 | 2.2723 | 2.2723 | 2.2723 | 2.2723 | 2.2723 | 2.2723 | 2.3723 | 2.3723 | 2.3723 | 2.3723 | 2.3723 | 2.3723 | 2.3723 | 2.3922 | 2.3922 | 2.3922 | 2.3922 | 2.3922 | 2.3922
| air velocity | 0.10747 | 0.11034 | 0.11462 | 0.1212 | 0.13079 | 0.14519 | 0.16239 | 0.097919 | 0.09941 | 0.10186 | 0.10569 | 0.11143 | 0.12033 | 0.13131 | 0.092744 | 0.093312 | 0.093972 | 0.095355 | 0.097965 | 0.10245
| Draft Rating | 8.855% | 0.092077 | 0.097354 | 0.10546 | 0.11734 | 0.13535 | 0.15726 | 7.674% | 7.859% | 8.162% | 8.635% | 9.342% | 10.44% | 11.8% | 7.03% | 7.101% | 7.184% | 7.356% | 7.68% | 8.235%
| PPD | 5.606% | 0.057258 | 0.059077 | 0.061926 | 0.06622 | 0.072999 | 0.081681 | 5.213% | 5.274% | 5.374% | 5.531% | 5.772% | 6.154% | 6.646% | 5.005% | 5.027% | 5.054% | 5.11% | 5.215% | 5.398%
PMV | bar: DN250 0 to DN500 5
| PPD class | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.3 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
| Spigot D | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250
| Spigot D | DN300 | DN300 | DN300 | DN300 | DN300 | DN300 | DN300 | DN300 | DN300 | DN300 | DN300 | DN300 | DN300 | DN300 | DN300 | DN300 | DN300 | DN300 | DN300 | DN300
Syntax Format
|  | DN250 | [6 empty] | DN355 | [6 empty] | DN500
|  | DN250-R0 | DN250-R1 | DN250-R2 | DN250-R3 | DN250-R4 | DN250-R5 | DN250-R6 | DN355-R0 | DN355-R1 | DN355-R2 | DN355-R3 | DN355-R4 | DN355-R5 | DN355-R6 | DN500-R0 | DN500-R1 | DN500-R2 | DN500-R3 | DN500-R4 | DN500-R5
| Spigot D | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250
| Max Airflow | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
| Max Recommended Airflow | 115.1 | 102.1 | 87.1 | 64.6 | 48.5 | 32.2 | 22.8 | 239.9 | 204.2 | 174.1 | 129.2 | 97 | 64.4 | 45.7 | 506.6 | 445 | 391.3 | 325.2 | 238.8 | 165.3
| Min Airflow | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
| Min Permissible Airflow | 23.8 | 20.8 | 17.1 | 13.2 | 9.7 | 6.7 | 4.7 | 47.8 | 41.6 | 34.1 | 26.4 | 19.4 | 13.5 | 9.5 | 95.3 | 86.2 | 77.5 | 63.9 | 47.6 | 32.7
Min % TD to | bar: DN250 0 to DN500 5
| Min Permissible % Turndown to | 19.8% | 17.3% | 14.2% | 11% | 8.1% | 5.6% | 3.9% | 39.9% | 34.7% | 28.5% | 22% | 16.2% | 11.2% | 7.9% | 79.4% | 71.8% | 64.6% | 53.2% | 39.7% | 27.2%
| Static Pressure | 38 | 48.3 | 66.5 | 120.7 | 214.4 | 486 | 966.4 | 8.8 | 12.1 | 16.6 | 30.2 | 53.6 | 121.5 | 241.6 | < 5 | < 5 | < 5 | < 5 | 8.8 | 18.4
| Total Pressure | 41.7 | 52 | 70.1 | 124.4 | 218 | 489.6 | 970.1 | 12.4 | 15.7 | 20.3 | 33.8 | 57.2 | 125.1 | 245.3 | 5.6 | 6.2 | 6.9 | 8.4 | 12.5 | 22.1
| Max Permissible P | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
| Sound Power Level | 44.6 | 47.3 | 50.8 | 57.6 | 64 | 73.2 | 80.9 | 27.2 | 32 | 37 | 40.8 | 46 | 54 | 60.1 | < 15 | < 15 | 22.2 | 24.1 | 27.9 | 33.8
| Sound Pressure Level | 29.6 | 32.3 | 35.8 | 42.6 | 49 | 58.2 | 65.9 | 12.2 | 17 | 22 | 25.8 | 31 | 39 | 45.1 | < 10 | < 10 | < 10 | < 10 | 12.9 | 18.8
| ΔT_max centre | 13.4 | 14.2 | 15.1 | 16.7 | 18 | 20 | 20 | 9.7 | 10.2 | 11.4 | 12.7 | 14.2 | 15.7 | 17.6 | 7.2 | 7.7 | 8.5 | 9.2 | 9.9 | 10.6
| ΔT_max (heating) perimeter | 9 | 9.5 | 10.1 | 11.1 | 12 | 13.5 | 14.5 | 6.5 | 6.8 | 7.6 | 8.4 | 9.5 | 10.5 | 11.7 | 4.8 | 5.1 | 5.6 | 6.1 | 6.6 | 7
| Cmax (centre) | 14.4 | 15 | 16.2 | 19.1 | 22.7 | - | - | 12.7 | 13 | 13.3 | 14 | 15.3 | 18.8 | 22.9 | 12.1 | 12.2 | 12.3 | 12.4 | 12.8 | 13.4
| Cmax (perimeter) | 12.9 | 13.5 | 14.6 | 17.2 | 22.7 | - | - | 11.5 | 11.6 | 12 | 12.6 | 13.8 | 17 | 22.9 | 10.9 | 11 | 11 | 11.2 | 11.5 | 12.1
| Cmin | 2.8 | 2.9 | 3 | 3.4 | 4.3 | - | - | 2.5 | 2.6 | 2.6 | 2.7 | 2.9 | 3.4 | 4.5 | 2.4 | 2.5 | 2.5 | 2.5 | 2.5 | 2.6
| Hmin | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4
| air velocity | 0.11 | 0.11 | 0.11 | 0.12 | 0.13 | - | - | 0.1 | 0.1 | 0.1 | 0.11 | 0.11 | 0.12 | 0.13 | 0.09 | 0.09 | 0.09 | 0.1 | 0.1 | 0.1
| Draft Rating | 0.089 | 0.092 | 0.097 | 0.105 | 0.117 | - | - | 0.077 | 0.079 | 0.082 | 0.086 | 0.093 | 0.104 | 0.118 | 0.07 | 0.071 | 0.072 | 0.074 | 0.077 | 0.082
| PPD | 0.056 | 0.057 | 0.059 | 0.062 | 0.066 | - | - | 0.052 | 0.053 | 0.054 | 0.055 | 0.058 | 0.062 | 0.066 | 0.05 | 0.05 | 0.051 | 0.051 | 0.052 | 0.054
| PMV | A | A | A | B | B | - | - | A | A | A | A | A | B | B | A | A | A | A | A | A
| PPD class | < 0.2 | < 0.2 | < 0.2 | < 0.2 | < 0.3 | < 0.3 | < 0.4 | < 0.2 | < 0.2 | < 0.2 | < 0.2 | < 0.2 | < 0.2 | < 0.3 | < 0.2 | < 0.2 | < 0.2 | < 0.2 | < 0.2 | < 0.2
| Spigot D | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250
| Spigot D | DN300 | DN300 | DN300 | DN300 | DN300 | DN300 | DN300 | DN300 | DN300 | DN300 | DN300 | DN300 | DN300 | DN300 | DN300 | DN300 | DN300 | DN300 | DN300 | DN300
Final Result Size Selection
1 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6
2 |  | DN355-R0 | DN355-R1 | DN355-R2 | DN355-R3 | DN355-R4 | DN355-R5 | DN355-R6
3 | Max Airflow | 120 | 120 | 120 | 120 | 120 | 120 | 120
4 | Max Permissible Airflow | 239.9 | 204.2 | 174.1 | 129.2 | 97 | 64.4 | 45.7
5 | Min Airflow | 120 | 120 | 120 | 120 | 120 | 120 | 120
6 | Min Permissible Airflow | 47.8 | 41.6 | 34.1 | 26.4 | 19.4 | 13.5 | 9.5
7 | Min % Turndown to | bar: 0 to 6
8 | Min Permissible % Turndown to | 0.399 | 0.347 | 0.285 | 0.22 | 0.162 | 0.112 | 0.079
9 | Static Pressure @ 100% Airflow [Pa] | 8.8 | 12.1 | 16.6 | 30.2 | 53.6 | 121.5 | 241.6
10 | Total Pressure @ 100% Airflow [Pa] | 12.4 | 15.7 | 20.3 | 33.8 | 57.2 | 125.1 | 245.3
11 | Max Permissible Total Pressure [Pa] | 35 | 35 | 35 | 35 | 35 | 35 | 35
12 | Sound Power Level [dB(A)] | 27.2 | 32 | 37 | 40.8 | 46 | 54 | 60.1
13 | Sound Pressure Level [NC] | 12.2 | 17 | 22 | 25.8 | 31 | 39 | 45.1
14 | Max ΔT (heating) - Centre Zone [K] | 9.7 | 10.2 | 11.4 | 12.7 | 14.2 | 15.7 | 17.6
15 | Max ΔT (heating) - Perimeter [K] | 6.5 | 6.8 | 7.6 | 8.4 | 9.5 | 10.5 | 11.7
16 | Max Centreline Distance [m] (centre) | 12.7 | 13 | 13.3 | 14 | 15.3 | 18.8 | 22.9
17 | Max Centreline Distance Perimeter [m] | 11.5 | 11.6 | 12 | 12.6 | 13.8 | 17 | 22.9
18 | Min Centreline Distance [m] | 2.5 | 2.6 | 2.6 | 2.7 | 2.9 | 3.4 | 4.5
19 | Min Permissible Diffuser Height [m] | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4
20 | Mean Room Air Velocity [m/s] | 0.1 | 0.1 | 0.1 | 0.11 | 0.11 | 0.12 | 0.13
21 | Mean Draught Rating (DR) | 0.077 | 0.079 | 0.082 | 0.086 | 0.093 | 0.104 | 0.118
22 | Mean PPD | 0.052 | 0.053 | 0.054 | 0.055 | 0.058 | 0.062 | 0.066
23 | Satisfies PPD Category (ISO7730) | bar: 0 to 6
24 | PMV | < 0.2 | < 0.2 | < 0.2 | < 0.2 | < 0.2 | < 0.2 | < 0.3
25 | Spigot D | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250
26 | Low profile spigot | DN300 | DN300 | DN300 | DN300 | DN300 | DN300 | DN300
Shading Rules
| High Pressure/Flow | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE |  | true=red
| Min Flow | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE |  | true = red
| max pressure/ min flow rejection | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE |  | true = gray
| SWL | 0 | 0 | 0 | 0 | 1 | 2 | 2 |  | 1 = orange, 2 = red
| ISNUMBER Cmin/Cmax | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
| Cmax Centre < Cmin | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
| Cmax Perimeter < Cmin | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | shade for any time Cmax < C min
| C min > Cmax | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | shade for any time Cmin > Cmax
| Cmax Centre vs C select | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
| Cmax Perim vs C Select | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | shade for any time C select > Cmax
| Cmin vs C Select | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | shade for any time C select < C min
| Perf Face | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
| Shading | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE
| ALL SHADED | 0: FALSE
| Perf Face Illegal | 0: 0
Notes
| heating | 0: Heating valid for specific flowrate of 2.3 L/s/m² (see Cells K17:K21) at 2.7 m height.
| comfort | 0: Comfort criteria for specific airflow rate of 2.3 L/s/m² (see Cells K17:K21) and room temperature of 23°C (Cell M23)
| min flowrate (converted) | 0: = 120; 1: 120
Cmax > C Selected
Cmin < C Selected
Cmin>Cmax
Spigot
AUNZ/DIN | bar: 0
| Max Airflow | 0: 120
DIN
|  | Standard | Max Airflow | Selection | Area |  |  | Low Profile | Selection | Area |  |  |  | Max | selection | Area
| 1 | DN150 | 50 | 0 | 0.017437 |  | 1 | 49.05 | 0 | 0.015551 |  | 1 | DN160 | 60.5 | 0 | 0.019856
| 2 | DN200 | 100 | 0 | 0.031103 |  | 2 | 82.78 | 0 | 0.023405 |  | 2 | DN200 | 100.5 | 0 | 0.031103
| 3 | DN250 | 160 | 1 | 0.048695 |  | 3 | 112.98 | 0 | 0.031259 |  | 3 | DN250 | 160.5 | 1 | 0.048695
| 4 | DN300 | 250 | 1 | 0.069763 |  | 4 | 154.18 | 1 | 0.039113 |  | 4 | DN315 | 260.5 | 1 | 0.07422
| 5 | DN350 | 350 | 1 | 0.093777 |  | 5 | 265.05 | 1 | 0.06456 |  | 5 | DN355 | 350.5 | 1 | 0.091483
| 6 | DN400 | 450 | 1 | 0.12074 |  | 6 | 385.12 | 1 | 0.093934 |  | 6 | DN400 | 9999 | 1 | 0.11654
| 7 | DN450 | 550 | 1 | 0.15623 |  | 7 | N/A |  |  |  | 7 | N/A
| 8 | 0: N/A
|  | 1: Standard; 2: 3; 6: Low Profile | 4 |  |  |  | Low Profile | 3
|  | 1: Spigot; 2: DN250; 6: Spigot | DN300 |  |  |  | Spigot | DN250
|  | 1: Area; 2: 0.048695; 6: Area | 0.039113 |  |  |  | Area | 0.048695
| Spigot Chosen Std | 0: DN250
| Spigot Chosen Low | 0: DN300
| Spigot V | 0: 2.4643
| Pd | 0: 3.6436

## Data (hidden)
Neck Sizes
DN250
DN355
DN500
Reducer
Reducer 0
Reducer 1
Reducer 2
Reducer 3
Reducer 4
Reducer 5
Reducer 6
Discharge Direction |  |  |  |  | 4 Way (360°)
4 Way (360°) | 4w |  |  |  | 4 Way | 4w
3 Way (270°) | 3w | for installations adjacent to wall |  |  | 3 Way | 3w
2 Way (2×90°) | 2s | for installation in hallways and corridors |  |  | 13 | 2s
2 Way (1×180°) | 2a | for installation in corners |  |  | 14 | 2a
Ceiling or Free | 1 | (1 = ceiling; 2 = free)
ADPI display
95%
90%
80%
70%
V
95% | 0.2
90% | 0.25
85% | 0.27
80% | 0.29 |  |  | Code
70% | 0.33 |  | 0 | 0
|  |  | 1 | R0
|  |  | 2 | R1
|  |  | 3 | R2
|  |  | 4 | R3
Code Generator |  |  | 5 | R4
Nominal Diameter | DN355 |  | 6 | R5
Reducer | 0 | 1 | 7 | R6
Reducer Validation | R0 |  | 8 | RA
Size & Reducer | DN355-R0
Face Shape
n | code | option | comment |  |  |  | DN250 |  |  | DN355 |  |  | DN500
0 | <face> | please select a valid face shape |  |  |  |  | Code | option | comment | Code | option | comment | Code | option | comment
1 | S595 | □ 595 mm square face* | □ 595 mm square face | □○ | ø | 1 | S295 | □ 295 mm square face | □ 295 mm square face | S595 | □ 595 mm square face | □ 595 mm square face | S595 | □ 595 mm square face | □ 595 mm square face
2 | C500 | ø 500 mm circular face | ø 500 mm circular face |  |  | 2 | C355 | ø 355 mm circular face | ø 355 mm circular face | C500 | ø 500 mm circular face | ø 500 mm circular face | C710 | ø 710 mm circular face | ø 710 mm circular face
3 | <face> | custom face size | custom face size (contact Smartair) |  |  | 3 | <face> | custom face size | custom face size (contact Smartair) | <face> | custom face size | custom face size (contact Smartair) | <face> | custom face size | custom face size (contact Smartair)
1 | S595 | □ 595 mm square face* | □ 595 mm square face |  |  | 4 | <face-n/a> | option not available | please select a valid face shape | <face-n/a> | option not available | option not available | <face-n/a> | option not available | option not available
[6 empty] | 1 | S295 | □ 295 mm square face | □ 295 mm square face | S595 | □ 595 mm square face | □ 595 mm square face | S595 | □ 595 mm square face | □ 595 mm square face
[6 empty] | 2 | C355 | ø 355 mm circular face | ø 355 mm circular face | C500 | ø 500 mm circular face | ø 500 mm circular face | C710 | ø 710 mm circular face | ø 710 mm circular face
[6 empty] | 3 | <face> | custom face size | custom face size (contact Smartair) | <face> | custom face size | custom face size (contact Smartair) | <face> | custom face size | custom face size (contact Smartair)
Discharge | 4w
Face finish | 0
Colour | RAL9003 | 1
Connection Type
1 | 0 | No connection box
2 | KF | Thermally insulated foam connection box with magnetic fastener & blanking cap
3 | KFR | Thermally insulated foam connection box with threaded rod fastener & cap
1 | 0 | No connection box
| Model | Size | Shape | Reducer | Discharge | Face Finish | Colour | Box
| SMARTEMP HSC-FD- | DN355- | S595- | R0- | 4w- | P0- | RAL9003- | 0
Non-Return Air | SMARTEMP HSC-FD-DN355-S595-R0-4w-P0-RAL9003-0
Return Air | SMARTEMP HSC-FD-DN355-S595-R0-P0-RAL9003-0
Order | SMARTEMP HSC-FD-DN355-S595-R0-4w-P0-RAL9003-0
Summary |  |  |  |  | ΔT
| Reducer Selected | 0 | Units | TEXT
1 | 0 | 0
2 | 0 | DN355-R0
3 | Max Airflow | 120 | L/s | 120 L/s @ 8.8 Pa static
4 | Max Permissible Airflow | 239.9 | L/s
5 | Min Airflow | 120 | L/s | 120 L/s (CAV)
6 | Min Permissible Airflow | 47.8 | L/s | 47.8 L/s (40%) @ ΔT = -12 K
7 | Min % Turndown to | 1
8 | Min Permissible % Turndown to | 39.9%
9 | Static Pressure @ 100% Airflow [Pa] | 8.8 | Pa
10 | Total Pressure @ 100% Airflow [Pa] | 12.4 | Pa
11 | Max Permissible Total Pressure [Pa] | 35
12 | Sound Power Level [dB(A)] | 27.2 |  | 27.2 dB(A)
13 | Sound Pressure Level [NC] | 12.2 |  | 12.2 NC
14 | Max ΔT (heating) - Centre Zone [K] | 9.7 |  | +9.7 K
15 | Max ΔT (heating) - Perimeter [K] | 6.5 |  | +6.5 K
16 | Max Centreline Distance [m] (centre) | 12.7 | m
17 | Max Centreline Distance Perimeter [m] | 11.5 | m
18 | Min Centreline Distance [m] | 2.5 | m
19 | Min Permissible Diffuser Height [m] | 2.4 | m
20 | Mean Room Air Velocity [m/s] | 0.1
21 | Mean Draught Rating (DR) | 0.077
22 | Mean PPD | 0.052
23 | Satisfies PPD Category (ISO7730) | A
24 | PMV | < 0.2
25 | Spigot D | DN250
26 | Low profile spigot | DN300 |  | DN300 (Low Profile Box)
27 | 0 | 0
28 | Shading Rules | 0
29 | High Pressure/Flow | FALSE
Other Selections and Notes
location note | Closed ceiling
heating note | +9.7 K (centre zones) / +6.5 K (perimeter zones)
heating heading | Max Heating ΔT @ 2.3 L/s/m²
return air
Diagram
| Cmin | Cmax (Centre) | Cmax (Perimeter)
| 2.5 | 12.7 | 11.5
C Max = 12.7 m / 11.5 m (centre/perimeter zones)
C Min = 2.5 m
Nomenclature | Nominal | M18
Nominal C
C select | 7.3
Nominal C = 7.3 m
Min Recommended Diffuser Height = 2.4 m
Selected Diffuser Height = 2.7 m
Spcific Flow Rate | 2.3 L/s/m²
Top Box 1 | C Max = 12.7 m / 11.5 m (centre/perimeter zones)
box 2 | C Min = 2.5 m | 1 | Specific Airflow Rate @ Nominal C = 2.3 L/s/m²
box 3 | Nominal C = 7.3 m | 2 | Specific Airflow Rate @ Selected C = 2.3 L/s/m²
room box | Specific Airflow Rate @ Nominal C = 2.3 L/s/m² | 3 | Selected Specific Airflow Rate: 2.3 L/s/m²
TEXT
ADPI | 90 |  | ≥ 90% ADPI
Room Temp | 23
Mean Room Air Velocity [m/s] | 0.1 | 0.1 | 0.1 m/s @ 2.3 L/s/m² (7.3 m spacing)
Mean Draught Rating (DR) | 7.7 | 0.077 | 7.7% @ room temperature of 23 ºC
Mean PPD | 5.2 | 0.052 | 5.2%
Satisfies PPD Category (ISO7730) | A | A | Category A
PMV | 0.2 | < 0.2 | -0.2 < PMV < +0.2
Description
| Diffuser size DN355 with no reducer | with no reducer
4 Way (360°) discharge
No perforated face plate
| Powder coated to RAL9003 | RAL9003

## Reducer Selector
SMARTEMP PRODUCT SELECTION CALCULATOR
Fixed Helical Swirl Diffuser [HSC-FD DN355 & DN500] |  |  | REDUCER Selector
| LEGEND: |  |  |  |  | INSTRUCTIONS:
| Warning |  |  |  |  | To add more rows, copy and insert rows as required from row 17 to row 37 (do not insert above row 17).
| Required Manual Input |  |  |  |  | Do not change formulae/values in columns F to Z, which in rows 17 to 37 are not protected (to allow copy and paste) but contain formulae that MUST NOT BE OVERWRITTEN.
Optional Manual Input
| Manual Input overwriting formula |  |  |  |  | Cells E17 to E37 may be overwritten with 355 or 500 to prevent automatic neck sizing.
[14 empty] | Tolerance: | [9 empty] | Tolerance:
Cooling: | dT.supply-room = |  | Turndown to | P.total Max = |  | Vmax | 221 | 192 | 158 | 122 | 90 | 62 | 44 | Vmin * |  | L/s | Vmax | 439 | 389 | 354 | 292 | 218 | 151 | Vmin *
(-8 to -16) | -12 | K | 30% | 35 | Pa | Vmin | 47.8 | 41.6 | 34.1 | 26.4 | 19.4 | 13.5 | 9.5 | 1 |  | L/s | Vmin | 95.3 | 86.2 | 77.5 | 63.9 | 47.6 | 32.7 | 1
|  | Max | Min |  | HSC-FD- | Vmax/Vmin | Reducer: | [6 empty] | 355 | 355 | HSC-FD- | Vmax/Vmin | Reducer: | [5 empty] | 500 | 500 | Remarks
Item | Qty | L/s | L/s | DN | DN355 | WARNING | 0 | 1 | 2 | 3 | 4 | 5 | 6 | Rmin | Rmax | DN500 | WARNING | 0 | 1 | 2 | 3 | 4 | 5 | Rmin | Rmax
eg. West Lobby | 1 | 120 | 36 | 355 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1
|  |  | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1
|  |  | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1
|  |  | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1
|  |  | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1
|  |  | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1
|  |  | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1
|  |  | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1
|  |  | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1
|  |  | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1
|  |  | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1
|  |  | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1
|  |  | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1
|  |  | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1
|  |  | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1
|  |  | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1
|  |  | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1
|  |  | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1
|  |  | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1
|  |  | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1
|  |  | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1
| 1 |  |  |  | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Notes
SMARTEMP PRODUCT SELECTION CALCULATOR
Fixed Helical Swirl Diffuser [HSC-FD DN250/DN355/DN500] Notes
Selection Notes
Total Pressure is inclusive of side-entry connection box pressure loss.
ΔT -ve denotes cooling
ΔT +ve denotes heating
Select desired comfort level (ADPI setting) to determine minimum and maximum centreline distance and minimum diffuser height.
Noise & Acoustic
Sound Pressure Level [NC] is an estimate for a single diffuser only located at 2.7 to 3.0 m height in a 70 m^3 space (typical office) with 10 dB(A) room absorption that is uniformly distributed, measured 2.1 m from the diffuser.
Sound Pressure Level is provided as a guide only for a standard, carpeted single office with acoustic ceiling. An acoustical engineer should be consulted for detailed calculations, especially for applications with more than one diffuser or where hard surfaces are involved.
Perforated Face
Perforated face (63% open area) only available for size DN355. Contact Smartair for custom perforations.
Diffuser as Return Air (R/A) Inlet
1. R/A diffuser pressure loss to be taken as equal to supply air static pressure.
2. R/A diffuser sound power level is up to 2 dB(A) greater than the supply air sound power level.
Layout & Discharge Pattern
Max and Min Centreline Distance is to be halved for spacing to walls or glazing.
|  | 4 Way (360°) |  |  | 3 Way (270°) |  |  | 2 Way (2×90°) |  |  | 2 Way (1×180°)
• | default |  | • | for installations adjacent to walls |  | • | for installations in corridors |  | • | for installations in corners
• | use when D > Cmin/2 |  | • | use when D < Cmin/2 |  | • | use when D < Cmin/2 |  | • | use when D < Cmin/2
Tender Text
Furnish and install SMARTEMP® Fixed Helical Swirl Diffusers, type HSC-FD, to provide diffuse airflow with fixed stable horizontal swirl discharge pattern for the provision of high thermal comfort. Each diffuser is to be made of powder coated steel and shall include 20 off-set radial vanes flush with the flat diffuser face. The diffuser shall be installed complete with a flush colour matching central cap and shall be suitable for ce ntral threaded rod connection. The diffuser face is to be square or round, as specified, and is to be fitted with the optional perforated screen where indicated. The diffuser is to be installed substantially flush with the suspended false ceiling or freely suspended, as specified. Swirl vanes are to include cambered leading edges for reduced noise and pressure drop, and helical swirl vane tips are each to have geometric twist to increase the airflow rate range of operation. Diffuser neck size is to be DN250, DN355 or DN500, as appropriate. Fit optional reducers where low airflow rates are required (DN355 and DN500 only). Install the diffusers at a discharge height of 2.4 to 4.5 m. For VAV applications, operate each diffuser within an airflow rate band turning down to no less than 25% at a ΔTsupply-room ≥ -16 K. For heating applications, observe ΔTsupply-room recommendations. Install segments covers (1/4; 2/4 opposed; 1/2) for diffuser placement near walls, in corridors or in corners. Connect each diffuser to SMARTEMP foam connections boxes, suitable for perimeter magnetic and/or central threaded rod connections, as specified.

## Plenum Box Details
SMARTEMP PRODUCT SELECTION CALCULATOR
Fixed Helical Swirl Diffuser [HSC-FD DN250/DN355/DN500] Notes
Recommended Plenum Box Details
ASNZ nominal sizes | Standard Plenum Box - Round & Ovalised Spigot | [6 empty] | 250 mm Low Profile Plenum Box - Ultra Ovalised Spigot
|  | Spigot Diameter | Spigot Height | Spigot End Radius | Spigot Width | Spigot Area (m2) |  |  |  | Spigot Height | Spigot End Radius | Spigot Width | Spigot Area (m2)
| H1 | Ø5 | H5 | R₁ | F |  |  |  | H1 | H5 | R₁ | F
DN150 | 300 | 149 |  |  |  | 0.017437 |  | DN150 | 250 | 100 | 50 | 177 | 0.015554
DN200 | 325 | 199 |  |  |  | 0.031103 |  | DN200 | 250 | 100 | 50 | 256 | 0.023454
DN250 | 350 | 249 |  |  |  | 0.048695 |  | DN250 | 250 | 100 | 50 | 334 | 0.031254
DN300 | 375 |  | 275 | 137.5 | 313 | 0.069846 |  | DN300 | 250 | 100 | 50 | 413 | 0.039154
DN350 | 400 |  | 300 | 150 | 377 | 0.093786 |  | DN350 | 250 | 150 | 75 | 463 | 0.064621
DN400 | 425 |  | 325 | 162.5 | 441 | 0.12066 |  | DN400 | 250 | 200 | 100 | 513 | 0.094016
|  |  | Round Spigot | [9 empty] | Low Profile Box
Ovalised Spigot
ALL DIMENSIONS IN mm
DIN nominal sizes | Round Spigot |  |  | Ovalised Spigot
|  | Spigot Diameter | Spigot Area (m2) |  |  |  | Spigot Height | Spigot End Radius | Spigot Width | Spigot Area (m2)
| H1 | Ø5 |  |  |  | H1 | H5 | R₁ | F
DN160 | 300 | 159 | 0.019856
DN200 | 325 | 199 | 0.031103
DN250 | 375 | 249 | 0.048695
DN315 | 440 | 314 | 0.077437 | DN315 ovalised |  | 375 | 250 | 125 | 351 | 0.074337
DN355 | 480 | 354 | 0.098423 | DN355 ovalised |  | 385 | 260 | 130 | 408 | 0.091573
DN400 | 525 | 399 | 0.12504 | DN400 ovalised |  | 420 | 295 | 147.5 | 458 | 0.11643

## layout diagrams (hidden)
Selection | 4w
4w
3w
2s
2a

## Selection Summary
HSC-FD Performance Calculator Summary
Project | <Project Name>
Company | <Name>
Client | <Name>
Product | SMARTEMP HSC-FD
Fixed Helical Swirl Diffuser
Size & Reducer | DN355-R0
Discharge Direction | 4 Way (360°)
Diffuser Location | Closed ceiling
Summary
Selected Airflow ¹ | 120 L/s @ 8.8 Pa static
Min Selected Airflow | 120 L/s (CAV)
Min Permissible Airflow | 47.8 L/s (40%) @ ΔT = -12 K
Max Heating ΔT @ 2.3 L/s/m² | +9.7 K (centre zones) / +6.5 K (perimeter zones)
Acoustic Performance |  | ¹ Values valid for diffuser including 'Standard Side Entry Plenum Box' with round spigot (refer to worksheet 'Notes and Drawings HSC-FD')
Sound Power Level ¹ | 27.2 dB(A)
Sound Pressure Level ^¹ | 12.2 NC | ^ based on 10 dB(A) room absorption
Recommended Plenum Box Spigot Diameter | DN250
DN300 (Low Profile Box)
Comfort Performance
Selected ADPI Target | ≥ 90% ADPI
Mean Room Air Velocity | 0.1 m/s @ 2.3 L/s/m² (7.3 m spacing)
Draught Rating (DR) | 7.7% @ room temperature of 23 ºC
PPD | 5.2%
Satisfies PPD (ISO7730) | Category A
Satisfies PMV * | -0.2 < PMV < +0.2
* ISO7730; ASHRAE Std 55
C Max = 12.7 m / 11.5 m (centre/perimeter zones)
C Min = 2.5 m
Nominal C = 7.3 m
Specific Airflow Rate @ Nominal C = 2.3 L/s/m²
Min Recommended Diffuser Height = 2.4 m
Selected Diffuser Height = 2.7 m
Configuration | Diffuser size DN355 with no reducer
□ 595 mm square face*
4 Way (360°) discharge
No perforated face plate
Powder coated to RAL9003
No connection box
Order Code | SMARTEMP HSC-FD-DN355-S595-R0-4w-P0-RAL9003-0 |  | v 10.14 [09/2025]