## LJC-AD
SMARTEMP PRODUCT SELECTION CALCULATOR
Linear Multi-Jet Ceiling Diffuser [LJC-AD]
Project: | <Project Name>
| Inputs | [7 empty] | Detailed Selection | [5 empty] | v 3.3 [02/2025]
| Maximum Airflow Rate | 100 | L/s/m | m3/h/m | ft³/min/ft |  |  |  |  | Air Pattern | 2-Way | 1-Way
| VAV (turndown to) | 100 | % | 10% to 100% (use 100% for CAV) |  |  |  |  | Draught Rating & Comfort | [6 empty] | Specific Airflow Rate (heating) | 5 | L/s/m2 | 2 to 10 L/s/m2 (default 5 L/s/m2)
| Maximum Permissible Static Pressure | 30 | Pa | default 30 Pa | [5 empty] | ADPI ≥ | 90% |  | default ≥ 90%
| ΔT (cooling) | -12 | K | 0K to -16K (default -12K) | [5 empty] | Diffuser Location | Closed Ceiling |  | Freely Suspended
| Diffuser Height | 2.7 | m | 2 m to 10 m (heating and cooling) |  |  |  |  | Diffuser Coverage = Average (Max, Min) 'C' Distance |  |  |  | see Distance section in Results (Row 60:62)
|  |  |  | 2 m to 15 m (cooling only) |  |  |  |  | OR |  | nominal distance = 9.9 m
| Active Length Ratio (see diagram) | 0.5 | * | 0.1 to 1.0 (default 0.5) | [5 empty] | Manual Diffuser Coverage | 7 | m | see 'C' in diagram below
[9 empty] | OR |  | average specific flow rate: 5.03 L/s/m²
[10 empty] | Specific Airflow Rate | 5 | L/s/m² | ≤ 30 L/s/m²
average diffuser coverage: 10 m
[10 empty] | Room Temperature (cooling) | 23 | °C | 20 °C to 26 °C (for draught rating)
Heating
[10 empty] | Room Temperature (heating) | 21 | °C | check for manual input
auto room temp. (heating) = 21 °C
[10 empty] | Room Temp. @ heating startup | 16 | °C | night setback temperature default (16 °C)
| Spigot Size | ASNZ Sizes (DN150; DN200; DN250; DN300; DN350) | [7 empty] | % Low Level Return (heating) | 0 | % | 0% to 100% (default 0%)
DIN Sizes (DN160; DN200; DN250; DN315; DN355)
See 'Notes' for resetting to default values
Related Products | [9 empty] | Thermal Comfort Guide
Smartemp LMC-AD: | for an identical look with slimmer profile; manual adjustment only | [8 empty] | ADPI ≥ 95%; ṽ ≤ 0.20 m/s: | Premium comfort, sedentary activity, such as in auditoria.
Smartemp LDB 12: | engineered by LTG for an ultra-slim look | [8 empty] | ADPI ≥ 90%; ṽ ≤ 0.25 m/s: | High comfort near-sedentary activity, such as in board rooms, high end offices and libraries.
Smartemp LDB 12 Clean: | engineered by LTG with SystemClean™ for minimal ceiling smudging and diffuser condensation | [8 empty] | ADPI ≥ 80%; ṽ ≤ 0.29 m/s: | Good comfort near sedentary activity, such as open-plan offices and meeting rooms.
Smartemp LDB 50 Maxx: | engineered by LTG for high flow rates | [8 empty] | ADPI ≥ 70%; ṽ ≤ 0.33 m/s: | Standard comfort medium activity, such as in transient spaces, retail and lobbies.
Smartemp LJW-AD: | for a wall-mounted solution; also available with electric and thermal actuator
Results | SMARTEMP LJC-AD |  |  | 1 Slot | 2 Slots | 3 Slots | 4 Slots | 5 Slots | 6 Slots | Key: | Suitable | Not Suitable | Warning
Airflow | Selected Airflow Rate |  | [L/s/m] | 100 | 100 | 100 | 100 | 100 | 100 |  | * Refer to 'Notes' worksheet for definitions and details
| Airflow @ Max Static Pressure |  | [L/s/m] | 53 | 108 | 164 | 228 | 283 | 339 |  | ** Refer to 'Dimensions & Connection Box' worksheet for details
| Min Selected Airflow |  | [L/s/m] | 100 | 100 | 100 | 100 | 100 | 100
| Min Permissible Airflow @ ΔT = -12K |  | [L/s/m] | 13.6 | 28.8 | 43.6 | 58.1 | 73.3 | 88.9
| Min % Turndown to |  |  | 100% | 100% | 100% | 100% | 100% | 100%
| Min Permissible % Turndown to |  |  | 14% | 29% | 44% | 58% | 73% | 89%
Pressure* | Static Pressure @ 100% Airflow |  | [Pa] | 107.8 | 25.9 | 11.2 | 5.8 | < 5 | < 5 | * Values valid for diffuser including side-entry connection box with round spigot (refer to 'Dimensions & Connection Box' sheet for details
| Total Pressure @ 100% Airflow |  | [Pa] | 127 | 28.4 | 12.4 | 7 | < 5 | < 5
| Max Selected Total Pressure |  | [Pa] | 30 | 30 | 30 | 30 | 30 | 30
Acoustics | Sound Power Level |  | [db(A)/m] | 44.9 | 36.9 | 29.2 | 21.2 | 16.9 | < 15 | - see 'Notes' for Sound Power/Pressure Level adjustment for other lengths
| Sound Pressure Level * |  | [NC/m] | 29.9 | 21.9 | 14.2 | < 10 | < 10 | < 10 | * Based on 10 dB room absorption (refer to 'Notes' sheet for details)
Cooling and Heating | Manually Adjusted Air Direction Setting: ** |  |  | A | A | A | A | A | A | Row 54: Direction setting for balanced cooling and heating performance
| Centre Zone: Heating ΔT Max |  | [K] | 15 | 15 | 15 | 15 | 15 | 15 | Rows 55:56: Typical max vertical temperature gradient 2 to 3°C/m Row 57: Typical vertical temperature gradient ≤ 1°C/m Vertical discharge: manual setting 'E' or with thermal/electric actuator. Thermal and electric actuator available for 2 slots or more only.
| Perimeter Zone: Heating ΔT Max |  | [K] | 15 | 15 | 15 | 15 | 13.3 | 11.6
Max (Vertical) Heating | ΔT Vertical Discharge: Setting 'E' |  | [K] | 20 | 20 | 20 | 13.8 | 9.3 | 6.7
Recommended Distances & Layout ** | Max Coverage Centre Zones (Cmax) |  | [m] | 19.7 | 15.8 | 14.6 | 14.1 | 13.7 | 13.5
| Max Coverage Perimeter Zones (Cmax) |  | [m] | 19.7 | 15.8 | 14.6 | 14.1 | 13.7 | 13.5
| Min Coverage (Cmin) |  | [m] | 8.3 | 5.4 | 4.9 | 4.7 | 4.6 | 4.5
| Min Diffuser Height |  | [m] | 2.3 | 2.4 | 2.4 | 2.5 | 2.5 | 2.6
Comfort | Mean Room Air Velocity |  | [m/s] | 0.17 | 0.15 | 0.14 | 0.14 | 0.13 | 0.13 | Comfort criteria valid for diffuser spacing of 9.9 m & room temperature of 23°C (see cells L18:L21 & L23)
| Mean Draught Rating (DR) |  |  | 16.7% | 13.8% | 12.9% | 12.4% | 12.1% | 11.9%
| Mean PPD |  |  | 8.6% | 7.4% | 7% | 6.9% | 6.7% | 6.7%
| ¦PMV¦ |  |  | < 0.4 | < 0.3 | < 0.3 | < 0.3 | < 0.3 | < 0.3
| Satisfies PPD Category (ISO7730) |  |  | B | B | B | B | B | B
T-Element | Thermal Element Setting |  | [°C] | Thermal/ Electric actuator avalable for 2+ slots only | n.r. | n.r. | 30† | 29 | 27 | n.r. - thermal element not recommended; consider electric actuator † - slightly elevated air velocities in heating ‡ - moderately elevated air velocities in heating Thermal Element for Heating When the thermal element is used, the space should always be warmed up from night setback using a supply air temperature greater than or equal to the thermal element setting (row 69), otherwise the guide-ring will retract and prevent heat projection to the floor. Consider introducing a Pre-Occupancy Warm-Up Boost mode. Pre Occupancy Warm-Up Boost - see ‘Notes’ rows 70-89
Pre-Occupancy Warm-up Boost | Warm-Up Max Boost ΔT |  | [K] |  |  |  | 14 | 13.3 | 10.7
| Warm-Up Airflow Boost Factor | [5 empty] | 1.009 | 1.1967 | 1.2643
| Warm-Up Pressure Boost Factor | [5 empty] | 1.0181 | 1.4321 | 1.5984
| Diffusers Active During Warm-Up Boost |  | % |  |  |  | 99.11% | 83.56% | 79.1%
Dimensions ** | Width Flangeless Face |  | [mm] | 43.5 | 85.5 | 127.5 | 169.5 | 211.5 | 253.5 | Refer to 'Dimensions & Connection Box' worksheet for details
| Width Flanged Face |  | [mm] | 72 | 114 | 156 | 198 | 240 | 282
| Width of Diffuser Throat |  | [mm] | 38 | 80 | 122 | 164 | 206 | 248
Spigot | Nominal Spigot Size / 1200 mm |  | [mm] | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | It is highly recommended to use multiple spigot connections. Spigot size/unit length can be downsized accordingly.
| Product Selection & Code Generator | [10 empty] | * indicates standard/default option
| Select model to create product code |  |  | 1 slot | 2 slots | 3 slots | 4 slots | 5 slots | 6 slots | custom |  | other slots available upon request
| Supply/Return |  |  | supply: adjustable direction |  |  | return air |  | return air boosted |  |  | see 'Notes' Row 16 for performance adjustments as a return air inlet
| Nominal Length |  |  | 1200* mm (neck) |  | 1195 mm (face) |  | custom^ ≤ 1200 mm (neck) |  |  |  | ^ contact Smartair Diffusion for custom lengths and colours
| Air Pattern Setting |  |  | 2-way blow selected (see Cell L9)
| Adjustment |  |  | manual | thermal actuator |  | electric actuator (24V, 2-10V) |  |  |  | electric actuator (24V, 3-pt) | manual adjustment only
| Air Direction Setting |  |  | recommended* | A (0 to -15°) |  | B (0 to -30°) | C (≈ -45°) | D (≈ -60°) | E (vertical) | custom | N/A for return air inlet
| Side Profile |  |  | with side flanges* |  | flangeless
| Diffuser Ends |  |  | 2 end flanges * |  | 1 end flange & 1 pair joining strips |  |  | 1 pair joining strips |  | no end flanges | joining strips for a continuous look
| Fixing |  |  | without accessories/by others * |  |  | expansion bracket |  | mounting frame for plasterboard
| Profile Colour |  |  | RAL9003* (signal white) |  | RAL9005 (jet black) |  | other ^
| Barrel Colour |  |  | black* | white
| Connection Box |  |  | no connection box * |  | uninsulated connection box |  |  | internally insulated connection box
[7 empty] | clipped to diffuser throat |  | screwed to diffuser throat |  |  | options only available with connection box
| Product Code |  | Please select length and number of slots | [6 empty] | more detailed options available in the LJC-AD product brochure
|  |  | • LJC-AD (supply air) • 1200 mm neck length; (number of slots not selected) • 2-way blow • discharge direction manually set to 'Air Pattern Setting' |  |  | • profile powder coated to RAL9003 with black barrels • with side flanges • with two end flanges • fixing by others; without accessories • no connection box |  |  |  | see 'Selection Summary & Print' for a printable summary of the selection
[6 empty] | click here to see product on smartair.asia | [7 empty] | Copyright © 2024 SMARTAIR DIFFUSION
Group Box 28
Group Box 35
Group Box 41
Group Box 38
Group Box 49
Group Box 72
Group Box 17
Group Box 121
Group Box 127
Group Box 130
Group Box 134
Group Box 24
Group Box 805
Group Box 1935
Group Box 53

## equations (hidden)
Units
| Length |  | Flow rate |  | Flow rate/unit length |  | Specific Flow rate |  | Pressure |  | temperature |  |  | Delta T |  |  | Length |  | velocity |  | acoustic
Selection | Unit | conv to SI | Unit | conv to SI | Unit | conv to SI | Unit | conv to SI | Unit | conv to SI | Unit |  | conv to SI | Unit |  | conv to SI | Unit | conv to SI | Unit | conv to SI |  |  | db(A) (addition)
1 | m | 1 | L/s | 1 | L/s/m | 1 | L/s/m² | 1 | Pa | 1 | °C | C | FALSE | K | 1 | FALSE | mm | 1 | m/s | 1 | db(A)/m | NC/m | 0
2 | m | 1 | m³/h | 0.27778 | m³/h/m | 0.27778 | m³/h/m² | 0.27778 | Pa | 1 | °C | C | FALSE | K | 1 | FALSE | mm | 1 | m/s | 1 | db(A)/m | NC/m | 0
3 | ft | 0.3048 | ft³/min | 0.47195 | ft³/min/ft | 1.5484 | ft³/min/ft² | 5.08 | inH₂O | 248.84 | °F | F | TRUE | ∆°F | 0.55556 | TRUE | in | 25.4 | ft/s | 0.3048 | db(A)/4ft | NC/4ft | 0.86075
Units | 1
Units Multiplier | m | 1 | L/s | 1 | L/s/m | 1 | L/s/m² | 1 | Pa | 1 | °C | C | FALSE | K | 1 | FALSE | mm | 1 | m/s | 1 | db(A)/m | NC/m | 0
Formatting | [m] | m/m | [L/s] | L/s/L/s | [L/s/m] | L/s/m/L/s/m | [L/s/m²] | L/s/m²/L/s/m² | [Pa] | Pa/Pa | [°C] | °C/°C |  | [K] | K/K |  | [mm] | mm/mm | [m/s] | m/s/m/s | [db(A)/m] | [NC/m] | NC/m/NC/m
Want
Input Values
Airflow Rate | 100 | L/s/m
VAV | 100
Max Total Pressure | 30 | Pa
dT(cooling) | -12 | °C
Room Height | 2.7 | m
Length Ratio | 0.5
Air Pattern | 2
Specific airflow | 5 | L/s/m²
ADPI | 0.9
LRA | 0
Ceiling | 1
Manual C distance | 7 | m
distance input type | 1
dT (Heating) | 12 | K
Room Temperature (cooling) | 23 | °C
Manual Supply Heating DT | FALSE
Manual Heating Temp | FALSE
Room Temp (heating) | 21 | °C
T night setback | 16 | °C
Input Validation and Conversion
Airflow Rate | 100 | L/s/m
VAV | 1
Airflow Rate (TD) | 100
Max Total Pressure | 30 | Pa
dT(cooling) | 12 | C
Diffuser Height | 2.7 | m
Length Ratio | 0.5
Air Pattern | 2
ADPI | 90%
Low level return multiplier | 0%
Local Velocity | 0.25
Ceiling Type | 0 | Closed
Ceiling Type Heating | 1
Manual C Distance | 7 | m
Specific airflow | 5 | m3/s/m2
Room Temperature (cooling) | 23 | C
Room Temp (heating) | 21 | C
T night setback | 16 | C
Room Temp (Heating) Selected/auto | 21 | C
[8 empty] | AU/NZ |  |  |  | DIN |  | v |  |  | I-P
Ceiling Type Hmin | 1 |  | H actual | Height Adjusted |  |  | 1 | 150 | 0.017671 | 0 | 1 | 160 | 0.020106 | 0 |  | 1 | 6 | 152.4 | 0.018241 | 0
Heating Height | 1.7 |  | 2.7 | 1.7 |  |  | 2 | 200 | 0.031416 | 0 | 2 | 200 | 0.031416 | 0 | 1.5625 | 2 | 7 | 177.8 | 0.024829 | 0
|  |  | 5 | 5 |  |  | 3 | 250 | 0.049087 | 2.4446 | 3 | 250 | 0.049087 | 2.4446 | 1.5625 | 3 | 10 | 254 | 0.050671 | 2.3682
|  |  | 1.4348 | -2.1739 |  |  | 4 | 300 | 0.070686 | 1.6977 | 4 | 315 | 0.077931 | 1.5398 | 1.5876 | 4 | 12 | 304.8 | 0.072966 | 1.6446
Draft Rating | 27.74% | [5 empty] | 5 | 350 | 0.096211 | 1.2473 | 5 | 355 | 0.09898 | 1.2124 | 1.2701 | 5 | 14 | 355.6 | 0.099315 | 1.2083
Global Distance | 9.9342 | [5 empty] | 6 | 400 | 0.12566 | 0.95493 | 6 | 400 | 0.12566 | 0.95493 | 1.2696 | 6 | 16 | 406.4 | 0.12972 | 0.92509
[7 empty] | 3 | 250 | 0.049087 | 2.4446 | 3 | 250 | 0.049087 | 2.4446 |  | 3 | 10 | 254 | 0.050671 | 2.3682
Spigot Selection | 1 |  | Selection | Spigot Size | Area | Velocity
Units Selection | 1 |  | 1 | 250 | 0.049087 | 2.4446 | mm
Spigot size | 250 | mm | 2 | 250 | 0.049087 | 2.4446 | mm
Spigot Area | 0.049087 | m2 | 3 | 10 | 0.050671 | 2.3682 | in
Spigot Velocity | 2.4446 | m/s
Cmin Ceiling Factor | 1
Cmax Ceiling Factor | 1
V_turndown | 100 |  | v_td=fr*vav
Diffuser Airflow for Neck Length | 120 | 1.2 | 1200
Hmin
Hmin 2WAY | 2.6012 |  | 0.04282 | 2.173
Hmin 1WAY | 2.7786
Hmin Select | 2.6012
ADPI
Hmin | 95% | 2.7012
| 90% | 2.6012
| 80% | 2.5012
| 70% | 2.4012
Cmin | 2-WAY |  |  |  | 1-WAY |  |  |  |  | Q' to v'
|  |  | Target Q'' |  |  |  | Target Q'' |  |  |  | 2-Way |  | 1-Way |  | Selection
H | ax | ^b | Q'' |  | ax | ^b | Q'' |  |  |  | ax | ^b | ax | ^b | ax | ^b
2.7 | 4510 | 2.2693 | 194.0536 |  | 2886 | 2.152 | 146.1044 |  |  | 2.7 | 0.02455 | 0.4405 | 0.02466 | 0.4647 | 0.02455 | 0.4405
4 | 3884 | 2.2426 | 173.4201 |  | 2651 | 2.175 | 129.9958 |  |  | 4 | 0.0251 | 0.4458 | 0.02669 | 0.4597 | 0.0251 | 0.4458
10.0001 | 3435 | 2.2754 | 146.5546 |  | 2317 | 2.194 | 110.664 |  |  | 10.0001 | 0.02797 | 0.4391 | 0.02927 | 0.4557 | 0.02797 | 0.4391
| Ax | ^b |  |  | Ax | ^b
2.7 | 235.858 | -0.20897 | 191.6493 | W/m2 | 176.5945 | -0.20573 | 143.9573 | W/m2
Q" allowed | 191.6493
v' for Vmax | 15.9708 | L/s/m2
v' for Vmin | 19.9708 | L/s/m2
v'' + correction factor | 4
Active Length Ratio Factor | 0.90063
Cmax
ADPI | for Vmax | for Vmin |  | Hfactor @ Vmax | Hfactor @ Vmin
95% | 1.91 | 2.54 |  | 5.317 | 4.4309
90% | 1.5 | 2 |  | 6 | 5
80% | 1 | 1.32 |  | 7.3659 | 6.1383
70% | 0.7 | 0.94 |  | 8.7318 | 7.2765 | [47 empty] | Q | SWL | P | A | B
at Vmax | 1.5 |  | at adpi | 6 | [48 empty] | 130 | 0 | 1.7881 | 15.324 | -2.6401
at Vmin | 2 |  |  | 5 | [48 empty] | 210 | 0 | 4.6659
[53 empty] | 280 | 0 | 8.2949
Cmax-Centre Zone
ADPI | for Vmax | for Vmin |  | Hfactor @ Vmax | Hfactor @ Vmin
95% | 1.5 | 2 |  | 5.317 | 4.4309
90% | 1.2152 | 1.6165 |  | 6 | 5
80% | 0.80587 | 1.0763 |  | 7.3659 | 6.1383
70% | 0.7 | 0.94 |  | 8.7318 | 7.2765
at Vmax | 1.2152 |  | at adpi | 6
at Vmin | 1.6165 |  |  | 5 | [48 empty] | 330 | 0 | 11.5218
Heating
Low level correction multiplier | 100%
adpi | T thermal correction |  | Min Thermal Setting
70% | 0 | 0.2 | 15
80% | 2 |  | 17
90% | 4 |  | 19
95% | 5 |  | 20
t-element-comfort correction | 4 |  | 19
Heating Height | Slope
2 | 1.0112 | [51 empty] | SWL | 3.0115
2.7 | 0.66726
3 | 0.54867
4 | 0.27434
5 | 0.088496
2.7 | 0.65159
Slot Size | 0.0195 | m
1Slot | [6 empty] | 2Slot | [6 empty] | 3Slot | [6 empty] | 4Slot | [5 empty] | 5Slot | [5 empty] | 6Slot | [5 empty] | 7Slot | [5 empty] | 8Slot
Slots | 1 | [5 empty] | Slots | 2 | [5 empty] | Slots | 3 | [5 empty] | Slots | 4 |  |  |  |  | Slots | 5 |  |  |  |  | Slots | 6 |  |  |  |  | Slots | 7 |  |  |  |  | Slots | 8
data.LMC.Flowrate | 35 | L/s/m |  |  |  |  | data.Flowrate | 74 | L/s/m |  |  |  |  | data.Flowrate | 112 | L/s/m |  |  |  |  | data.Flowrate | 149 | L/s/m |  |  |  | data.Flowrate | 188 | L/s/m |  |  |  | data.Flowrate | 228 | L/s/m |  |  |  | data.Flowrate | 265 | L/s/m |  |  |  | data.Flowrate | 304 | L/s/m
data.Flowrate | 52.5 | L/s/m |  |  |  |  | data.Flowrate | 111 | L/s/m |  |  |  |  | data.Flowrate | 168 | L/s/m |  |  |  |  | data.Flowrate | 223.5 | L/s/m |  |  |  | data.Flowrate | 282 | L/s/m |  |  |  | data.Flowrate | 342 | L/s/m |  |  |  | data.Flowrate | 397.5 | L/s/m |  |  |  | data.Flowrate | 456 | L/s/m
data.Total.Pressure | 35 | Pa |  |  |  |  | data.Pressure | 35 | Pa |  |  |  |  | data.Pressure | 35 | Pa |  |  |  |  | data.Pressure | 35 | Pa |  |  |  | data.Pressure | 35 | Pa |  |  |  | data.Pressure | 35 | Pa |  |  |  | data.Pressure | 35 | Pa |  |  |  | data.Pressure | 35 | Pa
data.Spigot.Diameter | 150 | [5 empty] | data.Spigot.Diameter | 250 | [5 empty] | data.Spigot.Diameter | 300 | [5 empty] | data.Spigot.Diameter | 300 |  |  |  |  | data.Spigot.Diameter | 350 |  |  |  |  | data.Spigot.Diameter | 400 |  |  |  |  | data.Spigot.Diameter | 400 |  |  |  |  | data.Spigot.Diameter | 450
data.Static Pressure | 29.594 | Pa |  |  |  |  | data.Static Pressure | 31.8681 | Pa |  |  |  |  | data.Static Pressure | 31.5401 | Pa |  |  |  |  | data.Static Pressure | 28.8765 | Pa |  |  |  | data.Static Pressure | 29.738 | Pa |  |  |  | data.Static Pressure | 30.4633 | Pa |  |  |  | data.Static Pressure | 25.1216 |  |  |  |  | data.Static Pressure | 22
spigot (nominal) velocity | 5.6588 | m/s |  |  |  |  | spigot (nominal) velocity | 2.0372 | m/s |  |  |  |  | spigot (nominal) velocity | 1.4147 | m/s |  |  |  |  | spigot (nominal) velocity | 1.4147 | m/s |  |  |  | spigot (nominal) velocity | 1.0394 | m/s |  |  |  | spigot (nominal) velocity | 0.79577 | m/s |  |  |  | spigot (nominal) velocity | 0.79577 | m/s |  |  |  | spigot (nominal) velocity | 0.62876 | m/s
Static Pressure @ Flowrate | 107.7706 | [5 empty] | Static Pressure @ Flowrate | 25.9167 | [5 empty] | Static Pressure @ Flowrate | 11.1999 | [5 empty] | Static Pressure @ Flowrate | 5.8058 |  |  |  |  | Static Pressure @ Flowrate | 3.753 |  |  |  |  | Static Pressure @ Flowrate | 2.6124 |  |  |  |  | Static Pressure @ Flowrate | 1.8351 |  |  |  |  | Static Pressure @ Flowrate | 1.446
Total Pressure @Flowrate | 126.9841 | Pa |  |  |  |  | Total Pressure @Flowrate | 28.4068 | Pa |  |  |  |  | Total Pressure @Flowrate | 12.4008 | Pa |  |  |  |  | Total Pressure @Flowrate | 7.0067 | Pa |  |  |  | Total Pressure @Flowrate | 4.4012 | Pa |  |  |  | Total Pressure @Flowrate | 2.9924 | Pa |  |  |  | Total Pressure @Flowrate | 2.2151 | Pa |  |  |  | Total Pressure @Flowrate | 1.6832 | Pa
Flowrate @MaxP | 52.8589 | [5 empty] | Flowrate @MaxP | 107.6975 | [5 empty] | Flowrate @MaxP | 163.8469 | [5 empty] | Flowrate @MaxP | 227.8062 |  |  |  |  | Flowrate @MaxP | 283.2396 |  |  |  |  | Flowrate @MaxP | 339.3893 |  |  |  |  | Flowrate @MaxP | 434.3844 |  |  |  |  | Flowrate @MaxP | 532.493
V_min | 13.6399 | V_min 30% for LMC2 (safety) |  |  |  |  | V_min | 28.8386 | [5 empty] | V_min | 43.6477 | [5 empty] | V_min | 58.067 |  |  |  |  | V_min | 73.2657 |  |  |  |  | V_min | 88.8542 |  |  |  |  | V_min | 103.2735 |  |  |  |  | V_min | 118.4723
Min % TD to | 13.64% | [5 empty] | Min % TD to | 28.84% | [5 empty] | Min % TD to | 43.65% | [5 empty] | Min % TD to | 58.07% |  |  |  |  | Min % TD to | 73.27% |  |  |  |  | Min % TD to | 88.85% |  |  |  |  | Min % TD to | 103.3% |  |  |  |  | Min % TD to | 118.5%
SWL - Static Pressure Coefficients | [6 empty] | SWL - Static Pressure Coefficients | [6 empty] | SWL - Static Pressure Coefficients | [6 empty] | SWL - Static Pressure Coefficients | [5 empty] | SWL - Static Pressure Coefficients | [5 empty] | SWL - Static Pressure Coefficients | [5 empty] | SWL - Static Pressure Coefficients | [5 empty] | SWL - Static Pressure Coefficients
A | 9.1038 | [5 empty] | A | 10.92 | [5 empty] | A | 12.23 | [5 empty] | A | 12.575 |  |  |  |  | A | 12.667 |  |  |  |  | A | 14.312 |  |  |  |  | A | 14.312 |  |  |  |  | A | 14.312
B(LMC1) | -2.4592 | +4.8 as guess from LMC1 to LMC2 |  |  |  |  | B | -3.4754 | [5 empty] | B | -5.1697 | [5 empty] | B | -5.7516 |  |  |  |  | B | -4.6794 |  |  |  |  | B | -8.6166 |  |  |  |  | B | -7.947 |  |  |  |  | B | -7.367
B(LMC2) | 2.3408 | [5 empty] | B(LMC2) | 1.3246 | [5 empty] | B(LMC2) | -0.3697 | [5 empty] | B(LMC2) | -0.9516 |  |  |  |  | B(LMC2) | 0.1206 |  |  |  |  | B(LMC2) | -3.8166 |  |  |  |  | B(LMC2) | -3.147 |  |  |  |  | B(LMC2) | -2.567
SWL | 44.9466 | [5 empty] | SWL | 36.868 | [5 empty] | SWL | 29.1769 | [5 empty] | SWL | 21.1661 |  |  |  |  | SWL | 16.8734 |  |  |  |  | SWL | 9.9269 |  |  |  |  | SWL | 5.5422 |  |  |  |  | SWL | 2.7113
SPL | 29.9466 |  | SWL-15 |  |  |  | SPL | 21.868 |  | SWL-15 |  |  |  | SPL | 14.1769 |  | SWL-15 |  |  |  | SPL | 6.1661 |  | SWL-15 |  |  | SPL | 1.8734 |  | SWL-15 |  |  | SPL | -5.0731 |  | SWL-15 |  |  | SPL | -9.4578 |  | SWL-15 |  |  | SPL | -12.2887 |  | SWL-15
Hmin
Hmin Factor | 0.9 | [5 empty] | Hmin Factor | 0.92 | [5 empty] | Hmin Factor | 0.94 | [5 empty] | Hmin Factor | 0.96 |  |  |  |  | Hmin Factor | 0.98 |  |  |  |  | Hmin Factor | 1 |  |  |  |  | Hmin Factor | 1 |  |  |  |  | Hmin Factor | 1
Min Diffuser Height (m) | 2.3411 | [5 empty] | Min Diffuser Height (m) | 2.3931 | [5 empty] | Min Diffuser Height (m) | 2.4451 | [5 empty] | Min Diffuser Height (m) | 2.4972 |  |  |  |  | Min Diffuser Height (m) | 2.5492 |  |  |  |  | Min Diffuser Height (m) | 2.6012 |  |  |  |  | Min Diffuser Height (m) | 2.6012 |  |  |  |  | Min Diffuser Height (m) | 2.6012
Distance Selection | [6 empty] | Distance Selection | [6 empty] | Distance Selection | [6 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection
Vmax | 52.5 | [5 empty] | Vmax | 111 | [5 empty] | Vmax | 168 | [5 empty] | Vmax | 223.5 |  |  |  |  | Vmax | 282 |  |  |  |  | Vmax | 342 |  |  |  |  | Vmax | 397.5 |  |  |  |  | Vmax | 456
Vmin | 15.75 | [5 empty] | Vmin | 33.3 | [5 empty] | Vmin | 50.4 | [5 empty] | Vmin | 67.05 |  |  |  |  | Vmin | 84.6 |  |  |  |  | Vmin | 102.6 |  |  |  |  | Vmin | 119.25 |  |  |  |  | Vmin | 136.8
Cmin | [6 empty] | Cmin | [6 empty] | Cmin | [6 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin
at V (L/s/m^2) | 10.8007 | [5 empty] | at V (L/s/m^2) | 16.5371 | [5 empty] | at V (L/s/m^2) | 18.2837 | [5 empty] | at V (L/s/m^2) | 19.1283 |  |  |  |  | at V (L/s/m^2) | 19.6587 |  |  |  |  | at V (L/s/m^2) | 20.0142 |  |  |  |  | at V (L/s/m^2) | 20.2475 |  |  |  |  | at V (L/s/m^2) | 20.4319
Cmin | 8.3386 | [5 empty] | Cmin | 5.4461 | [5 empty] | Cmin | 4.9258 | [5 empty] | Cmin | 4.7083 |  |  |  |  | Cmin | 4.5813 |  |  |  |  | Cmin | 4.4999 |  |  |  |  | Cmin | 4.4481 |  |  |  |  | Cmin | 4.4079
Cmax Perimeter | [6 empty] | Cmax Perimeter | [6 empty] | Cmax | [6 empty] | Cmax | [5 empty] | Cmax | [5 empty] | Cmax | [5 empty] | Cmax | [5 empty] | Cmax
v' @ V | 0.85374 | [5 empty] | v' @ V | 1.5708 | [5 empty] | v' @ V | 1.7891 | [5 empty] | v' @ V | 1.8947 |  |  |  |  | v' @ V | 1.961 |  |  |  |  | v' @ V | 2.0054 |  |  |  |  | v' @ V | 2.0346 |  |  |  |  | v' @ V | 2.0576
h factor @ V | 7.2925 | [5 empty] | h factor @ V | 5.8584 | [5 empty] | h factor @ V | 5.4218 | [5 empty] | h factor @ V | 5.2106 |  |  |  |  | h factor @ V | 5.078 |  |  |  |  | h factor @ V | 4.9891 |  |  |  |  | h factor @ V | 4.9308 |  |  |  |  | h factor @ V | 4.8847
Cmax | 58.5657 | [5 empty] | Cmax | 31.8312 | [5 empty] | Cmax | 27.9468 | [5 empty] | Cmax | 26.3895 |  |  |  |  | Cmax | 25.4973 |  |  |  |  | Cmax | 24.9323 |  |  |  |  | Cmax | 24.575 |  |  |  |  | Cmax | 24.2996
Cmax room height | 19.6898 | [5 empty] | Cmax room height | 15.8178 |  | ROOM TO INCLUDE FREE CEILING factor?? |  |  |  | Cmax room height | 14.6388 | [5 empty] | Cmax room height | 14.0686 |  |  |  |  | Cmax room height | 13.7106 |  |  |  |  | Cmax room height | 13.4707 |  |  |  |  | Cmax room height | 13.3132 |  |  |  |  | Cmax room height | 13.1887
Cmax Min of above | 19.6898 | final selection |  |  |  |  | Cmax Min of above | 15.8178 | final selection |  |  |  |  | Cmax Min of above | 14.6388 | final selection |  |  |  |  | Cmax Min of above | 14.0686 | final selection |  |  |  | Cmax Min of above | 13.7106 | final selection |  |  |  | Cmax Min of above | 13.4707 | final selection |  |  |  | Cmax Min of above | 13.3132 | final selection |  |  |  | Cmax Min of above | 13.1887 | final selection
Cmax centre zone | [6 empty] | Cmax centre zone | [6 empty] | Cmax centre zone | [6 empty] | Cmax centre zone | [5 empty] | Cmax centre zone | [5 empty] | Cmax centre zone | [5 empty] | Cmax centre zone | [5 empty] | Cmax centre zone
v' @ V | 0.69654 | [5 empty] | v' @ V | 1.272 | [5 empty] | v' @ V | 1.4473 | [5 empty] | v' @ V | 1.532 |  |  |  |  | v' @ V | 1.5852 |  |  |  |  | v' @ V | 1.6209 |  |  |  |  | v' @ V | 1.6443 |  |  |  |  | v' @ V | 1.6628
h factor @ V | 7.2925 | [5 empty] | h factor @ V | 5.8584 | [5 empty] | h factor @ V | 5.4218 | [5 empty] | h factor @ V | 5.2106 |  |  |  |  | h factor @ V | 5.078 |  |  |  |  | h factor @ V | 4.9891 |  |  |  |  | h factor @ V | 4.9308 |  |  |  |  | h factor @ V | 4.8847
Cmax | 71.7835 | [5 empty] | Cmax | 39.3067 | [5 empty] | Cmax | 34.5475 | [5 empty] | Cmax | 32.6366 |  |  |  |  | Cmax | 31.5411 |  |  |  |  | Cmax | 30.8471 |  |  |  |  | Cmax | 30.408 |  |  |  |  | Cmax | 30.0697
Cmax room height | 19.6898 | [5 empty] | Cmax room height | 15.8178 | [5 empty] | Cmax room height | 14.6388 | [5 empty] | Cmax room height | 14.0686 |  |  |  |  | Cmax room height | 13.7106 |  |  |  |  | Cmax room height | 13.4707 |  |  |  |  | Cmax room height | 13.3132 |  |  |  |  | Cmax room height | 13.1887
Cmax Min of above | 19.6898 | final selection |  |  |  |  | Cmax Min of above | 15.8178 | final selection |  |  |  |  | Cmax Min of above | 14.6388 | final selection |  |  |  |  | Cmax Min of above | 14.0686 | final selection |  |  |  | Cmax Min of above | 13.7106 | final selection |  |  |  | Cmax Min of above | 13.4707 | final selection |  |  |  | Cmax Min of above | 13.3132 | final selection |  |  |  | Cmax Min of above | 13.1887 | final selection
Comfort | [6 empty] | Comfort | [6 empty] | Comfort | [6 empty] | Comfort | [5 empty] | Comfort | [5 empty] | Comfort | [5 empty] | Comfort | [5 empty] | Comfort
global avg dist | [6 empty] | global avg dist | [6 empty] | global avg dist | [6 empty] | global avg dist | [5 empty] | global avg dist | [5 empty] | global avg dist | [5 empty] | global avg dist | [5 empty] | global avg dist
diffuser dist from spec. afr | [6 empty] | diffuser dist from spec. afr | [6 empty] | diffuser dist from spec. afr | [6 empty] | diffuser dist from spec. afr | [5 empty] | diffuser dist from spec. afr | [5 empty] | diffuser dist from spec. afr | [5 empty] | diffuser dist from spec. afr | [5 empty] | diffuser dist from spec. afr
diffuser dist selected | [6 empty] | diffuser dist selected | [6 empty] | diffuser dist selected | [6 empty] | diffuser dist selected | [5 empty] | diffuser dist selected | [5 empty] | diffuser dist selected | [5 empty] | diffuser dist selected | [5 empty] | diffuser dist selected
Area | [6 empty] | Area | [6 empty] | Area | [6 empty] | Area | [5 empty] | Area | [5 empty] | Area | [5 empty] | Area | [5 empty] | Area
v" | 5.0331 | L/s/m2 |  |  |  |  | v" | 5.0331 | L/s/m3 |  |  |  |  | v" | 5.0331 | L/s/m4 |  |  |  |  | v" | 5.0331 | L/s/m5 |  |  |  | v" | 5.0331 | L/s/m6 |  |  |  | v" | 5.0331 | L/s/m7 |  |  |  | v" | 5.0331 | L/s/m8 |  |  |  | v" | 5.0331 | L/s/m9
velocity adjustment |  |  | for total area |  |  |  | velocity adjustment |  |  | for total area |  |  |  | velocity adjustment |  |  | for total area |  |  |  | velocity adjustment |  |  | for total area |  |  | velocity adjustment |  |  | for total area |  |  | velocity adjustment |  |  | for total area |  |  | velocity adjustment |  |  | for total area |  |  | velocity adjustment |  |  | for total area
Q'' | 60.3971 | W/m2 |  |  |  |  | Q'' | 60.3971 | W/m3 |  |  |  |  | Q'' | 60.3971 | W/m4 |  |  |  |  | Q'' | 60.3971 | W/m5 |  |  |  | Q'' | 60.3971 | W/m6 |  |  |  | Q'' | 60.3971 | W/m7 |  |  |  | Q'' | 60.3971 | W/m8 |  |  |  | Q'' | 60.3971 | W/m9
v'' correction factor | -1.6263 | [5 empty] | v'' correction factor | 0.17813 | [5 empty] | v'' correction factor | 0.72757 | [5 empty] | v'' correction factor | 0.99327 |  |  |  |  | v'' correction factor | 1.1601 |  |  |  |  | v'' correction factor | 1.2719 |  |  |  |  | v'' correction factor | 1.3453 |  |  |  |  | v'' correction factor | 1.4033
v'' (adjusted) | 6.6594 | [5 empty] | v'' (adjusted) | 4.855 | [5 empty] | v'' (adjusted) | 4.3055 | [5 empty] | v'' (adjusted) | 4.0398 |  |  |  |  | v'' (adjusted) | 3.873 |  |  |  |  | v'' (adjusted) | 3.7612 |  |  |  |  | v'' (adjusted) | 3.6878 |  |  |  |  | v'' (adjusted) | 3.6298
Q'' (adjusted) | 79.9132 |  | no air density for max to mean velocity |  |  |  | Q'' (adjusted) | 58.2595 |  | no air density for max to mean velocity |  |  |  | Q'' (adjusted) | 51.6663 |  | no air density for max to mean velocity |  |  |  | Q'' (adjusted) | 48.4779 |  | no air density for max to mean velocity |  |  | Q'' (adjusted) | 46.4758 |  | no air density for max to mean velocity |  |  | Q'' (adjusted) | 45.1339 |  | no air density for max to mean velocity |  |  | Q'' (adjusted) | 44.2533 |  | no air density for max to mean velocity |  |  | Q'' (adjusted) | 43.5571 |  | no air density for max to mean velocity
2.7 | 0.1691 | [5 empty] | 2.7 | 0.14713 | [5 empty] | 2.7 | 0.13955 | [5 empty] | 2.7 | 0.13569 |  |  |  |  | 2.7 | 0.13319 |  |  |  |  | 2.7 | 0.13148 |  |  |  |  | 2.7 | 0.13034 |  |  |  |  | 2.7 | 0.12944
4 | 0.17695 | [5 empty] | 4 | 0.1537 | [5 empty] | 4 | 0.14569 | [5 empty] | 4 | 0.14161 |  |  |  |  | 4 | 0.13897 |  |  |  |  | 4 | 0.13717 |  |  |  |  | 4 | 0.13597 |  |  |  |  | 4 | 0.13501
10 | 0.19148 | [5 empty] | 10 | 0.16667 | [5 empty] | 10 | 0.15811 | [5 empty] | 10 | 0.15375 |  |  |  |  | 10 | 0.15093 |  |  |  |  | 10 | 0.149 |  |  |  |  | 10 | 0.14772 |  |  |  |  | 10 | 0.14669
For Room Height | Ax | B |  |  |  |  | For Room Height | Ax | B |  |  |  |  | For Room Height | Ax | B |  |  |  |  | For Room Height | Ax | B |  |  |  | For Room Height | Ax | B |  |  |  | For Room Height | Ax | B |  |  |  | For Room Height | Ax | B |  |  |  | For Room Height | Ax | B
| 0.15468 | 0.093366 | [5 empty] | 0.13438 | 0.094053 | [5 empty] | 0.12738 | 0.094314 | [5 empty] | 0.12382 | 0.094453 |  |  |  |  | 0.12152 | 0.094544 |  |  |  |  | 0.11994 | 0.094608 |  |  |  |  | 0.11889 | 0.094651 |  |  |  |  | 0.11806 | 0.094685
Velocity | 0.16971 | m/s |  |  |  |  | Velocity | 0.14754 | m/s |  |  |  |  | Velocity | 0.13989 | m/s |  |  |  |  | Velocity | 0.136 | m/s |  |  |  | Velocity | 0.13348 | m/s |  |  |  | Velocity | 0.13176 | m/s |  |  |  | Velocity | 0.13061 | m/s |  |  |  | Velocity | 0.1297 | m/s
Draught Rating | 16.67% | [5 empty] | Draught Rating | 13.83% | [5 empty] | Draught Rating | 12.87% | [5 empty] | Draught Rating | 12.38% |  |  |  |  | Draught Rating | 12.07% |  |  |  |  | Draught Rating | 11.85% |  |  |  |  | Draught Rating | 11.71% |  |  |  |  | Draught Rating | 11.6% |  |  |  |  | Draught Rating | #NUM!
PPD | 8.558% | [5 empty] | PPD | 7.415% | [5 empty] | PPD | 7.046% | [5 empty] | PPD | 6.862% |  |  |  |  | PPD | 6.746% |  |  |  |  | PPD | 6.666% |  |  |  |  | PPD | 6.614% |  |  |  |  | PPD | 6.572%
PPD Class | B | [5 empty] | PPD Class | B | [5 empty] | PPD Class | B | [5 empty] | PPD Class | B |  |  |  |  | PPD Class | B |  |  |  |  | PPD Class | B |  |  |  |  | PPD Class | B |  |  |  |  | PPD Class | B
PMV | 0.42774 | [5 empty] | PMV | 0.34317 | [5 empty] | PMV | 0.31053 | [5 empty] | PMV | 0.29307 |  |  |  |  | PMV | 0.28145 |  |  |  |  | PMV | 0.27334 |  |  |  |  | PMV | 0.26787 |  |  |  |  | PMV | 0.26346
PMV | 0.4 | [5 empty] | PMV | 0.3 | [5 empty] | PMV | 0.3 | [5 empty] | PMV | 0.3 |  |  |  |  | PMV | 0.3 |  |  |  |  | PMV | 0.3 |  |  |  |  | PMV | 0.3 |  |  |  |  | PMV | 0.3
ADPI ACTUAL | [6 empty] | ADPI ACTUAL | [6 empty] | ADPI ACTUAL | [6 empty] | ADPI ACTUAL | [5 empty] | ADPI ACTUAL | [5 empty] | ADPI ACTUAL | [5 empty] | ADPI ACTUAL | [5 empty] | ADPI ACTUAL
ADPI Actual Cmin | [6 empty] | ADPI Actual | [6 empty] | ADPI Actual | [6 empty] | ADPI Actual | [5 empty] | ADPI Actual | [5 empty] | ADPI Actual | [5 empty] | ADPI Actual | [5 empty] | ADPI Actual
Q'' (adjusted) for active length | 159.8265 | [5 empty] | Q'' (adjusted) for active length | 116.5191 | [5 empty] | Q'' (adjusted) for active length | 103.3325 | [5 empty] | Q'' (adjusted) for active length | 96.9559 |  |  |  |  | Q'' (adjusted) for active length | 92.9516 |  |  |  |  | Q'' (adjusted) for active length | 90.2677 |  |  |  |  | Q'' (adjusted) for active length | 88.5065 |  |  |  |  | Q'' (adjusted) for active length | 87.1142
2.7 | 0.22949 |  | (fix rounding errors) |  |  |  | 2.7 | 0.19966 | [5 empty] | 2.7 | 0.18938 | [5 empty] | 2.7 | 0.18414 |  |  |  |  | 2.7 | 0.18075 |  |  |  |  | 2.7 | 0.17843 |  |  |  |  | 2.7 | 0.17689 |  |  |  |  | 2.7 | 0.17566
4 | 0.24102 | [5 empty] | 4 | 0.20935 | [5 empty] | 4 | 0.19844 | [5 empty] | 4 | 0.19288 |  |  |  |  | 4 | 0.18929 |  |  |  |  | 4 | 0.18683 |  |  |  |  | 4 | 0.1852 |  |  |  |  | 4 | 0.18389
10 | 0.25961 | [5 empty] | 10 | 0.22597 | [5 empty] | 10 | 0.21436 | [5 empty] | 10 | 0.20845 |  |  |  |  | 10 | 0.20462 |  |  |  |  | 10 | 0.20201 |  |  |  |  | 10 | 0.20027 |  |  |  |  | 10 | 0.19888
For Room Height | Ax | B |  |  |  |  | For Room Height | Ax | B |  |  |  |  | For Room Height | Ax | B |  |  |  |  | For Room Height | Ax | B |  |  |  | For Room Height | Ax | B |  |  |  | For Room Height | Ax | B |  |  |  | For Room Height | Ax | B |  |  |  | For Room Height | Ax | B
| 0.2106 | 0.091859 | [5 empty] | 0.18296 | 0.092546 | [5 empty] | 0.17343 | 0.092807 | [5 empty] | 0.16858 | 0.092946 |  |  |  |  | 0.16545 | 0.093037 |  |  |  |  | 0.1633 | 0.093101 |  |  |  |  | 0.16187 | 0.093144 |  |  |  |  | 0.16074 | 0.093178
Velocity | 0.23 | m/s |  |  |  |  | Velocity | 0.2 | m/s |  |  |  |  | Velocity | 0.19 | m/s |  |  |  |  | Velocity | 0.18 | m/s |  |  |  | Velocity | 0.18 | m/s |  |  |  | Velocity | 0.18 | m/s |  |  |  | Velocity | 0.18 | m/s |  |  |  | Velocity | 0.18 | m/s
ADPI Cmin | 90% | [5 empty] | ADPI Cmin | 95% | [5 empty] | ADPI Cmin | 95% | [5 empty] | ADPI Cmin | 95% |  |  |  |  | ADPI Cmin | 95% |  |  |  |  | ADPI Cmin | 95% |  |  |  |  | ADPI Cmin | 95% |  |  |  |  | ADPI Cmin | 95%
Cmax Centre Zone | [6 empty] | Cmax Centre Zone | [6 empty] | Cmax Centre Zone | [6 empty] | Cmax Centre Zone | [5 empty] | Cmax Centre Zone | [5 empty] | Cmax Centre Zone | [5 empty] | Cmax Centre Zone | [5 empty] | Cmax Centre Zone
| v' | v distance | Hfactor | H distance |  |  |  | v' | v distance | Hfactor | H distance |  |  |  | v' | v distance | Hfactor | H distance |  |  |  | v' | v distance | Hfactor | H distance |  |  | v' | v distance | Hfactor | H distance |  |  | v' | v distance | Hfactor | H distance |  |  | v' | v distance | Hfactor | H distance |  |  | v' | v distance | Hfactor | H distance
95% | 0.85374 | 58.5657 | 6.4624 | 17.4486 |  |  | 95% | 1.5708 | 31.8312 | 5.1916 | 14.0173 |  |  | 95% | 1.7891 | 27.9468 | 4.8046 | 12.9725 |  |  | 95% | 1.8947 | 26.3895 | 4.6175 | 12.4673 |  | 95% | 1.961 | 25.4973 | 4.5 | 12.15 |  | 95% | 2.0054 | 24.9323 | 4.4212 | 11.9373 |  | 95% | 2.0346 | 24.575 | 4.3696 | 11.7978 |  | 95% | 2.0576 | 24.2996 | 4.3287 | 11.6875
90% | 0.69654 | 71.7835 | 7.2925 | 19.6898 |  |  | 90% | 1.272 | 39.3067 | 5.8584 | 15.8178 |  |  | 90% | 1.4473 | 34.5475 | 5.4218 | 14.6388 |  |  | 90% | 1.532 | 32.6366 | 5.2106 | 14.0686 |  | 90% | 1.5852 | 31.5411 | 5.078 | 13.7106 |  | 90% | 1.6209 | 30.8471 | 4.9891 | 13.4707 |  | 90% | 1.6443 | 30.408 | 4.9308 | 13.3132 |  | 90% | 1.6628 | 30.0697 | 4.8847 | 13.1887
80% | 0.45628 | 109.582 | 8.9527 | 24.1723 |  |  | 80% | 0.84417 | 59.2301 | 7.1921 | 19.4187 |  |  | 80% | 0.96227 | 51.9604 | 6.6561 | 17.9714 |  |  | 80% | 1.0194 | 49.0492 | 6.3968 | 17.2714 |  | 80% | 1.0552 | 47.3822 | 6.234 | 16.8319 |  | 80% | 1.0793 | 46.3269 | 6.1249 | 16.5373 |  | 80% | 1.0951 | 45.6595 | 6.0533 | 16.344 |  | 80% | 1.1075 | 45.1454 | 5.9967 | 16.1912
70% | 0.3898 | 128.2723 | 10.6129 | 28.6547 |  |  | 70% | 0.73398 | 68.122 | 8.5258 | 23.0197 |  |  | 70% | 0.83878 | 59.6107 | 7.8903 | 21.3039 |  |  | 70% | 0.88945 | 56.2143 | 7.583 | 20.4742 |  | 70% | 0.92128 | 54.2725 | 7.3901 | 19.9532 |  | 70% | 0.94261 | 53.0444 | 7.2607 | 19.604 |  | 70% | 0.9566 | 52.2682 | 7.1759 | 19.3748 |  | 70% | 0.96767 | 51.6706 | 7.1088 | 19.1937
Compare Cmax |  | 71.7835 |  | 19.6898 |  |  | Compare Cmax |  | 39.3067 |  | 15.8178 |  |  | Compare Cmax |  | 34.5475 |  | 14.6388 |  |  | Compare Cmax |  | 32.6366 |  | 14.0686 |  | Compare Cmax |  | 31.5411 |  | 13.7106 |  | Compare Cmax |  | 30.8471 |  | 13.4707 |  | Compare Cmax |  | 30.408 |  | 13.3132 |  | Compare Cmax |  | 30.0697 |  | 13.1887
Recommended Cmax | 19.7 | [5 empty] | Recommended Cmax | 15.8 | [5 empty] | Recommended Cmax | 14.6 | [5 empty] | Recommended Cmax | 14.1 |  |  |  |  | Recommended Cmax | 13.7 |  |  |  |  | Recommended Cmax | 13.5 |  |  |  |  | Recommended Cmax | 13.3 |  |  |  |  | Recommended Cmax | 13.2
Resultant ADPI from selected Cmax | ADPI | Selected Dist | Selected C Satisfies |  |  |  | Resultant ADPI from selected Cmax | ADPI | Selected Dist | Selected C Satisfies |  |  |  | Resultant ADPI from selected Cmax | ADPI | Selected Dist | Selected C Satisfies |  |  |  | Resultant ADPI from selected Cmax | ADPI | Selected Dist | Selected C Satisfies |  |  | Resultant ADPI from selected Cmax | ADPI | Selected Dist | Selected C Satisfies |  |  | Resultant ADPI from selected Cmax | ADPI | Selected Dist | Selected C Satisfies |  |  | Resultant ADPI from selected Cmax | ADPI | Selected Dist | Selected C Satisfies |  |  | Resultant ADPI from selected Cmax | ADPI | Selected Dist | Selected C Satisfies
| 95% | 17.4 | TRUE |  |  |  |  | 95% | 14 | TRUE |  |  |  |  | 95% | 13 | TRUE |  |  |  |  | 95% | 12.5 | TRUE |  |  |  | 95% | 12.1 | TRUE |  |  |  | 95% | 11.9 | TRUE |  |  |  | 95% | 11.8 | TRUE |  |  |  | 95% | 11.7 | TRUE
| 90% | 19.7 | TRUE |  |  |  |  | 90% | 15.8 | TRUE |  |  |  |  | 90% | 14.6 | TRUE |  |  |  |  | 90% | 14.1 | TRUE |  |  |  | 90% | 13.7 | TRUE |  |  |  | 90% | 13.5 | TRUE |  |  |  | 90% | 13.3 | TRUE |  |  |  | 90% | 13.2 | TRUE
| 80% | 24.2 | TRUE |  |  |  |  | 80% | 19.4 | TRUE |  |  |  |  | 80% | 18 | TRUE |  |  |  |  | 80% | 17.3 | TRUE |  |  |  | 80% | 16.8 | TRUE |  |  |  | 80% | 16.5 | TRUE |  |  |  | 80% | 16.3 | TRUE |  |  |  | 80% | 16.2 | TRUE
| 70% | 28.7 | TRUE |  |  |  |  | 70% | 23 | TRUE |  |  |  |  | 70% | 21.3 | TRUE |  |  |  |  | 70% | 20.5 | TRUE |  |  |  | 70% | 20 | TRUE |  |  |  | 70% | 19.6 | TRUE |  |  |  | 70% | 19.4 | TRUE |  |  |  | 70% | 19.2 | TRUE
| 0% | [6 empty] | 0% | [6 empty] | 0% | [6 empty] | 0% | [5 empty] | 0% | [5 empty] | 0% | [5 empty] | 0% | [5 empty] | 0%
ADPI Satisfied | 95% | [5 empty] | ADPI Satisfied | 95% | [5 empty] | ADPI Satisfied | 95% | [5 empty] | ADPI Satisfied | 95% |  |  |  |  | ADPI Satisfied | 95% |  |  |  |  | ADPI Satisfied | 95% |  |  |  |  | ADPI Satisfied | 95% |  |  |  |  | ADPI Satisfied | 95%
ADPI Cmax (perimeter) | Use turndown flow rate | [5 empty] | ADPI Cmax (perimeter) | Use turndown flow rate | [5 empty] | ADPI Cmax (perimeter) | Use turndown flow rate | [5 empty] | ADPI Cmax (perimeter) | Use turndown flow rate |  |  |  |  | ADPI Cmax (perimeter) | Use turndown flow rate |  |  |  |  | ADPI Cmax (perimeter) | Use turndown flow rate |  |  |  |  | ADPI Cmax (perimeter) | Use turndown flow rate |  |  |  |  | ADPI Cmax (perimeter) | Use turndown flow rate
Flowrates | 52.5 | 15.75 |  |  |  |  | Flowrates | 111 | 33.3 |  |  |  |  | Flowrates | 168 | 50.4 |  |  |  |  | Flowrates | 223.5 | 67.05 |  |  |  | Flowrates | 282 | 84.6 |  |  |  | Flowrates | 342 | 102.6 |  |  |  | Flowrates | 397.5 | 119.25 |  |  |  | Flowrates | 456 | 136.8
Cmax Perimeter | [6 empty] | Cmax Perimeter | [6 empty] | Cmax Perimeter | [6 empty] | Cmax Perimeter | [5 empty] | Cmax Perimeter | [5 empty] | Cmax Perimeter | [5 empty] | Cmax Perimeter | [5 empty] | Cmax Perimeter
| v' | v distance | Hfactor | H distance |  |  |  | v' | v distance | Hfactor | H distance |  |  |  | v' | v distance | Hfactor | H distance |  |  |  | v' | v distance | Hfactor | H distance |  |  | v' | v distance | Hfactor | H distance |  |  | v' | v distance | Hfactor | H distance |  |  | v' | v distance | Hfactor | H distance |  |  | v' | v distance | Hfactor | H distance
95% | 1.0957 | 45.6323 | 6.4624 | 17.4486 |  |  | 95% | 1.9992 | 25.0101 | 5.1916 | 14.0173 |  |  | 95% | 2.2743 | 21.9849 | 4.8046 | 12.9725 |  |  | 95% | 2.4073 | 20.77 | 4.6175 | 12.4673 |  | 95% | 2.4909 | 20.0735 | 4.5 | 12.15 |  | 95% | 2.5468 | 19.6322 | 4.4212 | 11.9373 |  | 95% | 2.5836 | 19.353 | 4.3696 | 11.7978 |  | 95% | 2.6126 | 19.1378 | 4.3287 | 11.6875
90% | 0.85374 | 58.5657 | 7.2925 | 19.6898 |  |  | 90% | 1.5708 | 31.8312 | 5.8584 | 15.8178 |  |  | 90% | 1.7891 | 27.9468 | 5.4218 | 14.6388 |  |  | 90% | 1.8947 | 26.3895 | 5.2106 | 14.0686 |  | 90% | 1.961 | 25.4973 | 5.078 | 13.7106 |  | 90% | 2.0054 | 24.9323 | 4.9891 | 13.4707 |  | 90% | 2.0346 | 24.575 | 4.9308 | 13.3132 |  | 90% | 2.0576 | 24.2996 | 4.8847 | 13.1887
80% | 0.58639 | 85.2668 | 8.9527 | 24.1723 |  |  | 80% | 1.0453 | 47.833 | 7.1921 | 19.4187 |  |  | 80% | 1.185 | 42.1929 | 6.6561 | 17.9714 |  |  | 80% | 1.2526 | 39.9168 | 6.3968 | 17.2714 |  | 80% | 1.295 | 38.609 | 6.234 | 16.8319 |  | 80% | 1.3235 | 37.7793 | 6.1249 | 16.5373 |  | 80% | 1.3421 | 37.254 | 6.0533 | 16.344 |  | 80% | 1.3569 | 36.8489 | 5.9967 | 16.1912
70% | 0.3898 | 128.2723 | 10.6129 | 28.6547 |  |  | 70% | 0.73398 | 68.122 | 8.5258 | 23.0197 |  |  | 70% | 0.83878 | 59.6107 | 7.8903 | 21.3039 |  |  | 70% | 0.88945 | 56.2143 | 7.583 | 20.4742 |  | 70% | 0.92128 | 54.2725 | 7.3901 | 19.9532 |  | 70% | 0.94261 | 53.0444 | 7.2607 | 19.604 |  | 70% | 0.9566 | 52.2682 | 7.1759 | 19.3748 |  | 70% | 0.96767 | 51.6706 | 7.1088 | 19.1937
Compare Cmax |  | 58.5657 |  | 19.6898 |  |  | Compare Cmax |  | 31.8312 |  | 15.8178 |  |  | Compare Cmax |  | 27.9468 |  | 14.6388 |  |  | Compare Cmax |  | 26.3895 |  | 14.0686 |  | Compare Cmax |  | 25.4973 |  | 13.7106 |  | Compare Cmax |  | 24.9323 |  | 13.4707 |  | Compare Cmax |  | 24.575 |  | 13.3132 |  | Compare Cmax |  | 24.2996 |  | 13.1887
Recommended Cmax | 19.7 | [5 empty] | Recommended Cmax | 15.8 | [5 empty] | Recommended Cmax | 14.6 | [5 empty] | Recommended Cmax | 14.1 |  |  |  |  | Recommended Cmax | 13.7 |  |  |  |  | Recommended Cmax | 13.5 |  |  |  |  | Recommended Cmax | 13.3 |  |  |  |  | Recommended Cmax | 13.2
Resultant ADPI from selected Cmax | ADPI | Selected Dist | Selected C Satisfies |  |  |  | Resultant ADPI from selected Cmax | ADPI | Selected Dist | Selected C Satisfies |  |  |  | Resultant ADPI from selected Cmax | ADPI | Selected Dist | Selected C Satisfies |  |  |  | Resultant ADPI from selected Cmax | ADPI | Selected Dist | Selected C Satisfies |  |  | Resultant ADPI from selected Cmax | ADPI | Selected Dist | Selected C Satisfies |  |  | Resultant ADPI from selected Cmax | ADPI | Selected Dist | Selected C Satisfies |  |  | Resultant ADPI from selected Cmax | ADPI | Selected Dist | Selected C Satisfies |  |  | Resultant ADPI from selected Cmax | ADPI | Selected Dist | Selected C Satisfies
| 95% | 17.4 | TRUE |  |  |  |  | 95% | 14 | TRUE |  |  |  |  | 95% | 13 | TRUE |  |  |  |  | 95% | 12.5 | TRUE |  |  |  | 95% | 12.1 | TRUE |  |  |  | 95% | 11.9 | TRUE |  |  |  | 95% | 11.8 | TRUE |  |  |  | 95% | 11.7 | TRUE
| 90% | 19.7 | TRUE |  |  |  |  | 90% | 15.8 | TRUE |  |  |  |  | 90% | 14.6 | TRUE |  |  |  |  | 90% | 14.1 | TRUE |  |  |  | 90% | 13.7 | TRUE |  |  |  | 90% | 13.5 | TRUE |  |  |  | 90% | 13.3 | TRUE |  |  |  | 90% | 13.2 | TRUE
| 80% | 24.2 | TRUE |  |  |  |  | 80% | 19.4 | TRUE |  |  |  |  | 80% | 18 | TRUE |  |  |  |  | 80% | 17.3 | TRUE |  |  |  | 80% | 16.8 | TRUE |  |  |  | 80% | 16.5 | TRUE |  |  |  | 80% | 16.3 | TRUE |  |  |  | 80% | 16.2 | TRUE
| 70% | 28.7 | TRUE |  |  |  |  | 70% | 23 | TRUE |  |  |  |  | 70% | 21.3 | TRUE |  |  |  |  | 70% | 20.5 | TRUE |  |  |  | 70% | 20 | TRUE |  |  |  | 70% | 19.6 | TRUE |  |  |  | 70% | 19.4 | TRUE |  |  |  | 70% | 19.2 | TRUE
| 0% | [6 empty] | 0% | [6 empty] | 0% | [6 empty] | 0% | [5 empty] | 0% | [5 empty] | 0% | [5 empty] | 0% | [5 empty] | 0%
ADPI Satisfied | 95% | [5 empty] | ADPI Satisfied | 95% | [5 empty] | ADPI Satisfied | 95% | [5 empty] | ADPI Satisfied | 95% |  |  |  |  | ADPI Satisfied | 95% |  |  |  |  | ADPI Satisfied | 95% |  |  |  |  | ADPI Satisfied | 95% |  |  |  |  | ADPI Satisfied | 95%
COMBINED SELECTED ADPI (Centre) | 90% | [5 empty] | COMBINED SELECTED ADPI (Centre) | 95% | [5 empty] | COMBINED SELECTED ADPI (Centre) | 95% | [5 empty] | COMBINED SELECTED ADPI (Centre) | 95% |  |  |  |  | COMBINED SELECTED ADPI (Centre) | 95% |  |  |  |  | COMBINED SELECTED ADPI (Centre) | 95% |  |  |  |  | COMBINED SELECTED ADPI (Centre) | 95% |  |  |  |  | COMBINED SELECTED ADPI (Centre) | 95%
COMBINED SELECTED ADPI (Perim) | 90% | [5 empty] | COMBINED SELECTED ADPI (Perim) | 95% | [5 empty] | COMBINED SELECTED ADPI (Perim) | 95% | [5 empty] | COMBINED SELECTED ADPI (Perim) | 95% |  |  |  |  | COMBINED SELECTED ADPI (Perim) | 95% |  |  |  |  | COMBINED SELECTED ADPI (Perim) | 95% |  |  |  |  | COMBINED SELECTED ADPI (Perim) | 95% |  |  |  |  | COMBINED SELECTED ADPI (Perim) | 95%
Heating 1 Slot | [6 empty] | Heating 2 Slot | [6 empty] | Heating 3 slot | [6 empty] | Heating 4 slot | [5 empty] | Heating 5 slot | [5 empty] | Heating 6 slot | [5 empty] | Heating 7 slot | [5 empty] | Heating 8 slot
heating X "A" * LN | 8.0647 | [5 empty] | heating X "A" * LN | 7.3278 | [5 empty] | heating X "A" * LN | 6.8968 | [5 empty] | heating X "A" * LN | 6.5909 |  |  |  |  | heating X "A" * LN | 6.3537 |  |  |  |  | heating X "A" * LN | 6.1599 |  |  |  |  | heating X "A" * LN | 5.996 |  |  |  |  | heating X "A" * LN | 5.854
heating X + "B" | -25.687 | [5 empty] | heating X + "B" | -24.934 | [5 empty] | heating X + "B" | -24.493 | [5 empty] | heating X + "B" | -24.181 |  |  |  |  | heating X + "B" | -23.938 |  |  |  |  | heating X + "B" | -23.74 |  |  |  |  | heating X + "B" | -23.573 |  |  |  |  | heating X + "B" | -23.427
heatingX | 11.4523 | [5 empty] | heatingX | 8.8118 | [5 empty] | heatingX | 7.2679 | [5 empty] | heatingX | 6.1712 |  |  |  |  | heatingX | 5.3219 |  |  |  |  | heatingX | 4.6274 |  |  |  |  | heatingX | 4.0396 |  |  |  |  | heatingX | 3.5317
heatingSlope | 0.65159 | [5 empty] | heatingSlope | 0.65159 | [5 empty] | heatingSlope | 0.65159 | [5 empty] | heatingSlope | 0.65159 |  |  |  |  | heatingSlope | 0.65159 |  |  |  |  | heatingSlope | 0.65159 |  |  |  |  | heatingSlope | 0.65159 |  |  |  |  | heatingSlope | 0.65159
heatingY | 7.4622 | [5 empty] | heatingY | 5.7417 | [5 empty] | heatingY | 4.7357 | [5 empty] | heatingY | 4.0211 |  |  |  |  | heatingY | 3.4677 |  |  |  |  | heatingY | 3.0152 |  |  |  |  | heatingY | 2.6322 |  |  |  |  | heatingY | 2.3012
heating_dT(10K) | 16.5828 |  |  | 2.2222 |  |  | heating_dT(10K) | 12.758 |  |  | 2.222 |  |  | heating_dT(10K) | 10.5228 |  |  | 2.222 |  |  | heating_dT(10K) | 8.9349 |  |  | 2.222 |  | heating_dT(10K) | 7.7052 |  |  | 2.222 |  | heating_dT(10K) | 6.6997 |  |  | 2.222 |  | heating_dT(10K) | 5.8487 |  |  | 2.222 |  | heating_dT(10K) | 5.1133 |  |  | 2.222
(old) heating @ dT | 14.3284 |  | -0.00451 | 0.09517 | 0.4993 |  | heating @ dT | 11.0236 |  | -0.00451 | 0.09517 | 0.4993 |  | heating @ dT | 9.0922 |  | -0.00451 | 0.09517 | 0.4993 |  | heating @ dT | 7.7202 |  | -0.00451 | 0.09517 | 0.4993 | heating @ dT | 6.6577 |  | -0.00451 | 0.09517 | 0.4993 | heating @ dT | 5.7889 |  | -0.00451 | 0.09517 | 0.4993 | heating @ dT | 5.0536 |  | -0.00451 | 0.09517 | 0.4993 | heating @ dT | 4.4181 |  | -0.00451 | 0.09517 | 0.4993
heating dT (perimeter) | 28.6567 | [5 empty] | heating dT (perimeter) | 22.0472 | [5 empty] | heating dT (perimeter) | 18.1845 | [5 empty] | heating dT (perimeter) | 15.4405 |  |  |  |  | heating dT (perimeter) | 13.3154 |  |  |  |  | heating dT (perimeter) | 11.5778 |  |  |  |  | heating dT (perimeter) | 10.1071 |  |  |  |  | heating dT (perimeter) | 8.8363
heating dT (centre) | 42.9851 | [5 empty] | heating dT (centre) | 33.0708 | [5 empty] | heating dT (centre) | 27.2767 | [5 empty] | heating dT (centre) | 23.1607 |  |  |  |  | heating dT (centre) | 19.9731 |  |  |  |  | heating dT (centre) | 17.3667 |  |  |  |  | heating dT (centre) | 15.1607 |  |  |  |  | heating dT (centre) | 13.2544
Heating in D setting (unused) | [6 empty] | Heating in D setting (unused) | [6 empty] | Heating in D setting (unused) | [6 empty] | Heating in D setting (unused) | [5 empty] | Heating in D setting (unused) | [5 empty] | Heating in D setting (unused) | [5 empty] | Heating in D setting (unused) | [5 empty] | Heating in D setting (unused)
k-factor | 0.90058 | [5 empty] | k-factor | 0.77213 | [5 empty] | k-factor | 0.70567 | [5 empty] | k-factor | 0.66201 |  |  |  |  | k-factor | 0.63001 |  |  |  |  | k-factor | 0.60502 |  |  |  |  | k-factor | 0.58467 |  |  |  |  | k-factor | 0.56759
H-n (exit width) | 0.0195 | [5 empty] | H-n (exit width) | 0.039 | [5 empty] | H-n (exit width) | 0.0585 | [5 empty] | H-n (exit width) | 0.078 |  |  |  |  | H-n (exit width) | 0.0975 |  |  |  |  | H-n (exit width) | 0.117 |  |  |  |  | H-n (exit width) | 0.1365 |  |  |  |  | H-n (exit width) | 0.156
dT (Vertical) | 119.1261 | K |  |  |  |  | dT (Vertical) | 33.4364 | K |  |  |  |  | dT (Vertical) | 15.9017 | K |  |  |  |  | dT (Vertical) | 9.3849 | K |  |  |  | dT (Vertical) | 6.2344 | K |  |  |  | dT (Vertical) | 4.4633 | K |  |  |  | dT (Vertical) | 3.3647 | K |  |  |  | dT (Vertical) | 2.6342 | K
dT (Vertical) Low level corrected | 119.1261 | K |  |  |  |  | dT (Vertical) Low level corrected | 33.4364 | K |  |  |  |  | dT (Vertical) Low level corrected | 15.9017 | K |  |  |  |  | dT (Vertical) Low level corrected | 9.3849 | K |  |  |  | dT (Vertical) Low level corrected | 6.2344 | K |  |  |  | dT (Vertical) Low level corrected | 4.4633 | K |  |  |  | dT (Vertical) Low level corrected | 3.3647 | K |  |  |  | dT (Vertical) Low level corrected | 2.6342 | K
Heating for Vertical | [6 empty] | Heating for Vertical | [6 empty] | Heating for Vertical | [6 empty] | Heating for Vertical | [5 empty] | Heating for Vertical | [5 empty] | Heating for Vertical | [5 empty] | Heating for Vertical | [5 empty] | Heating for Vertical
k-factor | 1.104 | [5 empty] | k-factor | 0.971 | [5 empty] | k-factor | 0.901 | [5 empty] | k-factor | 0.854 |  |  |  |  | k-factor | 0.82 |  |  |  |  | k-factor | 0.792 |  |  |  |  | k-factor | 0.77 |  |  |  |  | k-factor | 0.751
H-n (exit width) | 0.0195 | [5 empty] | H-n (exit width) | 0.039 | [5 empty] | H-n (exit width) | 0.0585 | [5 empty] | H-n (exit width) | 0.078 |  |  |  |  | H-n (exit width) | 0.0975 |  |  |  |  | H-n (exit width) | 0.117 |  |  |  |  | H-n (exit width) | 0.1365 |  |  |  |  | H-n (exit width) | 0.156
dT (Vertical) | 161.6889 | K |  |  |  |  | dT (Vertical) | 47.1531 | K |  |  |  |  | dT (Vertical) | 22.942 | K |  |  |  |  | dT (Vertical) | 13.7507 | K |  |  |  | dT (Vertical) | 9.2575 | K |  |  |  | dT (Vertical) | 6.6848 | K |  |  |  | dT (Vertical) | 5.0853 | K |  |  |  | dT (Vertical) | 4.0091 | K
dT (Vertical) Low level corrected | 161.6889 | K |  |  |  |  | dT (Vertical) Low level corrected | 47.1531 | K |  |  |  |  | dT (Vertical) Low level corrected | 22.942 | K |  |  |  |  | dT (Vertical) Low level corrected | 13.7507 | K |  |  |  | dT (Vertical) Low level corrected | 9.2575 | K |  |  |  | dT (Vertical) Low level corrected | 6.6848 | K |  |  |  | dT (Vertical) Low level corrected | 5.0853 | K |  |  |  | dT (Vertical) Low level corrected | 4.0091 | K
Horizontal>Vertical | [6 empty] | Horizontal>Vertical | [6 empty] | Horizontal>Vertical | [6 empty] | Horizontal>Vertical | [5 empty] | Horizontal>Vertical | [5 empty] | Horizontal>Vertical | [5 empty] | Horizontal>Vertical | [5 empty] | Horizontal>Vertical
editting vertical | 161.6889 | K |  |  |  |  | editting vertical | 47.1531 | K |  |  |  |  | editting vertical | 22.942 | K |  |  |  |  | editting vertical | 13.7507 | K |  |  |  | editting vertical | 9.2575 | K |  |  |  | editting vertical | 6.6848 | K |  |  |  | editting vertical | 5.0853 | K |  |  |  | editting vertical | 4.0091 | K
heating (centre) | 42.9851 | K |  |  |  |  | heating (centre) | 33.0708 | K |  |  |  |  | heating (centre) | 22.942 | K |  |  |  |  | heating (centre) | 13.7507 | K |  |  |  | heating (centre) | 9.2575 | K |  |  |  | heating (centre) | 6.6848 | K |  |  |  | heating (centre) | 5.0853 | K |  |  |  | heating (centre) | 4.0091 | K
heating (perimeter) | 28.6567 | K |  |  |  |  | heating (perimeter) | 22.0472 | K |  |  |  |  | heating (perimeter) | 15.2947 | K |  |  |  |  | heating (perimeter) | 9.1671 | K |  |  |  | heating (perimeter) | 6.1716 | K |  |  |  | heating (perimeter) | 4.4565 | K |  |  |  | heating (perimeter) | 3.3902 | K |  |  |  | heating (perimeter) | 2.6728 | K
Heating Penetration | 9.6261 | m |  |  |  |  | Heating Penetration | 4.2332 | m |  |  |  |  | Heating Penetration | 2.6187 | m |  |  |  |  | Heating Penetration | 1.8616 | m |  |  |  | Heating Penetration | 1.43 | m |  |  |  | Heating Penetration | 1.1509 | m |  |  |  | Heating Penetration | 0.95912 | m |  |  |  | Heating Penetration | 0.81852 | m
Thermal Element
comfort corrected thermal element DT | 165.6889 | K |  |  |  |  | comfort corrected thermal element DT | 51.1531 | K |  |  |  |  | comfort corrected thermal element DT | 26.942 | K |  |  |  |  | comfort corrected thermal element DT | 17.7507 | K |  |  |  | comfort corrected thermal element DT | 13.2575 | K |  |  |  | comfort corrected thermal element DT | 10.6848 | K |  |  |  | comfort corrected thermal element DT | 9.0853 | K |  |  |  | comfort corrected thermal element DT | 8.0091 | K
T.element setting | 181.6889 | [5 empty] | T.element setting | 67.1531 | [5 empty] | T.element setting | 42.942 | [5 empty] | T.element setting | 33.7507 |  |  |  |  | T.element setting | 29.2575 |  |  |  |  | T.element setting | 26.6848 |  |  |  |  | T.element setting | 25.0853 |  |  |  |  | T.element setting | 24.0091
T.e. setting not rounded | n.r. | [5 empty] | T.e. setting not rounded | n.r. | [5 empty] | T.e. setting not rounded | n.r. | [5 empty] | T.e. setting not rounded | 30 |  |  |  |  | T.e. setting not rounded | 29.2575 |  |  |  |  | T.e. setting not rounded | 26.6848 |  |  |  |  | T.e. setting not rounded | 25.0853 |  |  |  |  | T.e. setting not rounded | 24.0091
T element setting | n.r. | [5 empty] | T element setting | n.r. | [5 empty] | T element setting | n.r. | [5 empty] | T element setting | 30 |  |  |  |  | T element setting | 29 |  |  |  |  | T element setting | 27 |  |  |  |  | T element setting | 25 |  |  |  |  | T element setting | 24
T- element Note | [6 empty] | T- element Note | [6 empty] | T- element Note | [6 empty] | T- element Note | † |  |  |  |  | T- element Note | [5 empty] | T- element Note | [5 empty] | T- element Note | [5 empty] | T- element Note
T-el Velocity category | [6 empty] | T-el Velocity category | [6 empty] | T-el Velocity category | [6 empty] | T-el Velocity category | mid |  |  |  |  | T-el Velocity category | [5 empty] | T-el Velocity category | [5 empty] | T-el Velocity category | [5 empty] | T-el Velocity category
Warm-up Boost | [6 empty] | Warm-up Boost | [6 empty] | Warm-up Boost | [6 empty] | Warm-up Boost | [5 empty] | Warm-up Boost | [5 empty] | Warm-up Boost | [5 empty] | Warm-up Boost | [5 empty] | Warm-up Boost
Warm-up DT to Te setting | #VALUE! | [5 empty] | Warm-up DT to Te setting | #VALUE! | [5 empty] | Warm-up DT to Te setting | #VALUE! | [5 empty] | Warm-up DT to Te setting | 14 |  |  |  |  | Warm-up DT to Te setting | 13.2575 |  |  |  |  | Warm-up DT to Te setting | 10.6848 |  |  |  |  | Warm-up DT to Te setting | 9.0853 |  |  |  |  | Warm-up DT to Te setting | 8.0091
Actual max DT | 20 | [5 empty] | Actual max DT | 20 | [5 empty] | Actual max DT | 20 | [5 empty] | Actual max DT | 13.7507 |  |  |  |  | Actual max DT | 9.2575 |  |  |  |  | Actual max DT | 6.6848 |  |  |  |  | Actual max DT | 5.0853 |  |  |  |  | Actual max DT | 4.0091
Choose DT Warm-up | #VALUE! | [5 empty] | Choose DT Warm-up | #VALUE! | [5 empty] | Choose DT Warm-up | #VALUE! | [5 empty] | Choose DT Warm-up | 14 |  |  |  |  | Choose DT Warm-up | 13.2575 |  |  |  |  | Choose DT Warm-up | 10.6848 |  |  |  |  | Choose DT Warm-up | 9.0853 |  |  |  |  | Choose DT Warm-up | 8.0091
Airflow boost | [6 empty] | Airflow boost | [6 empty] | Airflow boost | [6 empty] | Airflow boost | 1.009 |  |  |  |  | Airflow boost | 1.1967 |  |  |  |  | Airflow boost | 1.2643 |  |  |  |  | Airflow boost | 1.3366 |  |  |  |  | Airflow boost | 1.4134
Pressure boost | [6 empty] | Pressure boost | [6 empty] | Pressure boost | [6 empty] | Pressure boost | 1.0181 |  |  |  |  | Pressure boost | 1.4321 |  |  |  |  | Pressure boost | 1.5984 |  |  |  |  | Pressure boost | 1.7866 |  |  |  |  | Pressure boost | 1.9977
Diffusers active | [6 empty] | Diffusers active | [6 empty] | Diffusers active | [6 empty] | Diffusers active | 0.99105 |  |  |  |  | Diffusers active | 0.83563 |  |  |  |  | Diffusers active | 0.79097 |  |  |  |  | Diffusers active | 0.74815 |  |  |  |  | Diffusers active | 0.70751
heating dT 'E' | 57.3135 | [5 empty] | heating dT 'E' | 44.0944 | [5 empty] | heating dT 'E' | 36.369 | [5 empty] | heating dT 'E' | 30.881 |  |  |  |  | heating dT 'E' | 26.6308 |  |  |  |  | heating dT 'E' | 23.1556 |  |  |  |  | heating dT 'E' | 20.2143 |  |  |  |  | heating dT 'E' | 17.6726
1Slot | [6 empty] | 2Slot | [6 empty] | 3Slot | [6 empty] | 4Slot | [5 empty] | 5Slot | [5 empty] | 6Slot | [5 empty] | 7Slot | [5 empty] | 8Slot
Global Distance | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Cmax | 19.6898 | 15.8178 | 14.6388 | 14.0686 | 13.7106 | 13.4707 | 13.3132 | 13.1887
Cmin | 8.3386 | 5.4461 | 4.9258 | 4.7083 | 4.5813 | 4.4999 | 4.4481 | 4.4079
Accept | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE
Accept cmax |  | 15.8178 | 14.6388 | 14.0686 |  |  |  |  | 14.8417
accept cmin |  | 5.4461 | 4.9258 | 4.7083 |  |  |  |  | 5.0268
if all rejected | 19.6898 | 15.8178 | 14.6388 | 14.0686 | 13.7106 | 13.4707 | 13.3132 | 13.1887 | 15.2327
if all rejected | 8.3386 | 5.4461 | 4.9258 | 4.7083 | 4.5813 | 4.4999 | 4.4481 | 4.4079 | 5.4167
Average | 9.9342
Final Distance Selections
Distance (from avg) | 9.9342
diffuser dist from spec. afr | 10 | m
diffuser dist from spec. afr converted | 10 | m
Selected Dist | 9.9342 | m
Selected Dist converted | 9.9342 | m
Area (incl active length) | 19.8685 | m2
v" (incl active length) | 5.0331 | L/s/m2
v" adj for heating | 5.0331 | L/s/m2
v" (incl active length)units | 5.0331 | L/s/m² | (converted)
v" (incl active length) (for display/units) | 5.03 | L/s/m² | (converted)
Air Pattern Settings | 2 WAY | 1 WAY
1 | A | AB | A
2 | B | AC | B
3 | C | BC | C
A
Pre-Results
Slots | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Max Airflow (L/s/m) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Max Recommended Airflow (L/s) | 52.8589 | 107.6975 | 163.8469 | 227.8062 | 283.2396 | 339.3893 | 434.3844 | 532.493
Min Airflow (L/s/m) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Min Permissible Airflow | 13.6399 | 28.8386 | 43.6477 | 58.067 | 73.2657 | 88.8542 | 103.2735 | 118.4723
Min % Turndown to | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Min Permissible % Turndown to | 13.64% | 28.84% | 43.65% | 58.07% | 73.27% | 88.85% | 1.0327 | 1.1847
Max Static Pressure (Pa) | 107.7706 | 25.9167 | 11.1999 | 5.8058 | 3.753 | 2.6124 | 1.8351 | 1.446
Max Total Pressure (Pa) | 126.9841 | 28.4068 | 12.4008 | 7.0067 | 4.4012 | 2.9924 | 2.2151 | 1.6832
Max Permissible Pressure (Pa) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Sound Power Level (dBA) | 44.9466 | 36.868 | 29.1769 | 21.1661 | 16.8734 | 9.9269 | 5.5422 | 2.7113
Sound Pressure Level (NC) | 29.9466 | 21.868 | 14.1769 | 6.1661 | 1.8734 | -5.0731 | -9.4578 | -12.2887
Air Pattern Setting | A | A | A | A | A | A | A | A
Max Permissible ΔT (centre) (K) | 42.9851 | 33.0708 | 27.2767 | 23.1607 | 19.9731 | 17.3667 | 15.1607 | 13.2544
Max Permissible ΔT (heating) (K) | 28.6567 | 22.0472 | 18.1845 | 15.4405 | 13.3154 | 11.5778 | 10.1071 | 8.8363
Max Permissible ΔT ('E') (K) | 161.6889 | 47.1531 | 22.942 | 13.7507 | 9.2575 | 6.6848 | 5.0853 | 4.0091
Max Coverage Dist Centre Zone [m] | 19.6898 | 15.8178 | 14.6388 | 14.0686 | 13.7106 | 13.4707 | 13.3132 | 13.1887
Max C/L Distance (m) Perimeter | 19.6898 | 15.8178 | 14.6388 | 14.0686 | 13.7106 | 13.4707 | 13.3132 | 13.1887
Min C/L Distance (m) | 8.3386 | 5.4461 | 4.9258 | 4.7083 | 4.5813 | 4.4999 | 4.4481 | 4.4079
Min Diffuser Height (m) | 2.3411 | 2.3931 | 2.4451 | 2.4972 | 2.5492 | 2.6012 | 2.6012 | 2.6012
Mean Room Air V | 0.16971 | 0.14754 | 0.13989 | 0.136 | 0.13348 | 0.13176 | 0.13061 | 0.1297
Draught Rating | 16.67% | 0.13832 | 0.1287 | 0.12383 | 0.12069 | 0.11855 | 0.11712 | 0.11599
PPD | 8.558% | 0.074145 | 0.070456 | 0.068624 | 0.067455 | 0.066663 | 0.06614 | 0.065723
PPD Class | B | B | B | B | B | B | B | B
PMV | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Thermal element setting | n.r. | n.r. | n.r. | 30 | 29 | 27 | 25 | 24
Thermal element note |  |  |  | †
Warm-Up Max Boost DT | #VALUE! | #VALUE! | #VALUE! | 14 | 13.2575 | 10.6848 | 9.0853 | 8.0091
Warm-Up Airflow Boost |  |  |  | 1.009 | 1.1967 | 1.2643 | 1.3366 | 1.4134
Warm-Up Pressure Boost |  |  |  | 1.0181 | 1.4321 | 1.5984 | 1.7866 | 1.9977
Diffusers Active During Warm-Up Boost |  |  |  | 0.99105 | 0.83563 | 0.79097 | 0.74815 | 0.70751
Nominal Spigot Size | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250
ADPI actual (centre) | 90% | 95% | 95% | 95% | 95% | 95% | 95% | 95%
ADPI actual (perim) | 90% | 95% | 95% | 95% | 95% | 95% | 95% | 95%
Results unit conv.
Slots | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Selected Airflow L/s/m | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Airflow @ Max Static Pressure L/s/m | 52.8589 | 107.6975 | 163.8469 | 227.8062 | 283.2396 | 339.3893 | 434.3844 | 532.493
Min Selected Airflow L/s/m | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Min Permissible Airflow @ -12 K | 13.6399 | 28.8386 | 43.6477 | 58.067 | 73.2657 | 88.8542 | 103.2735 | 118.4723
Min % Turndown to | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Min Permissible % Turndown to | 13.64% | 28.84% | 43.65% | 58.07% | 73.27% | 88.85% | 103.3% | 118.5%
Max Static Pressure Pa | 107.7706 | 25.9167 | 11.1999 | 5.8058 | 3.753 | 2.6124 | 1.8351 | 1.446
Max Total Pressure [Pa] | 126.9841 | 28.4068 | 12.4008 | 7.0067 | 4.4012 | 2.9924 | 2.2151 | 1.6832
Max Permissible Pressure (Pa) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Sound Power Level [db(A)/m] | 44.9466 | 36.868 | 29.1769 | 21.1661 | 16.8734 | 9.9269 | 5.5422 | 2.7113
Sound Pressure Level [NC/m] | 29.9466 | 21.868 | 14.1769 | 6.1661 | 1.8734 | -5.0731 | -9.4578 | -12.2887
Air Pattern Setting | A | A | A | A | A | A | A | A
Heating Centre Zones with Direction 'AK | 42.9851 | 33.0708 | 27.2767 | 23.1607 | 19.9731 | 17.3667 | 15.1607 | 13.2544
Heating Perimeter Zones with Direction 'AK | 28.6567 | 22.0472 | 18.1845 | 15.4405 | 13.3154 | 11.5778 | 10.1071 | 8.8363
Max Permissible ΔT (heating) E [K | 161.6889 | 47.1531 | 22.942 | 13.7507 | 9.2575 | 6.6848 | 5.0853 | 4.0091
Max Coverage Dist Centre Zone [m | 19.6898 | 15.8178 | 14.6388 | 14.0686 | 13.7106 | 13.4707 | 13.3132 | 13.1887
Max C/L Distance Perimeter [m | 19.6898 | 15.8178 | 14.6388 | 14.0686 | 13.7106 | 13.4707 | 13.3132 | 13.1887
Min C/L Distance [m | 8.3386 | 5.4461 | 4.9258 | 4.7083 | 4.5813 | 4.4999 | 4.4481 | 4.4079
Min Diffuser Height [m | 2.3411 | 2.3931 | 2.4451 | 2.4972 | 2.5492 | 2.6012 | 2.6012 | 2.6012
Mean Room Air V m/s | 0.16971 | 0.14754 | 0.13989 | 0.136 | 0.13348 | 0.13176 | 0.13061 | 0.1297
Draught Rating | 16.67% | 13.83% | 12.87% | 12.38% | 12.07% | 11.85% | 11.71% | 11.6%
PPD | 8.558% | 7.415% | 7.046% | 6.862% | 6.746% | 6.666% | 6.614% | 6.572%
PMV | B | B | B | B | B | B | B | B
PPD Class | 40% | 30% | 30% | 30% | 30% | 30% | 30% | 30%
Thermal Element Setting | n.r. | n.r. | n.r. | 30 | 29 | 27 | 25 | 24
thermal element note |  |  |  | †
Warm-Up Max Boost DT | #VALUE! | #VALUE! | #VALUE! | 14 | 13.2575 | 10.6848 | 9.0853 | 8.0091
Warm-Up Airflow Boost |  |  |  | 100.9% | 119.7% | 126.4% | 133.7% | 141.3%
Warm-Up Pressure Boost |  |  |  | 101.8% | 143.2% | 159.8% | 178.7% | 199.8%
Diffusers Active During Warm-Up Boost |  |  |  | 99.11% | 83.56% | 79.1% | 74.81% | 70.75%
Nominal Spigot Size | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250
ADPI actual (centre)
ADPI actual (perim)
Results
Slots | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Selected Airflow [L/s] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Airflow @ Max Static Pressure[L/s] | 53 | 108 | 164 | 228 | 283 | 339 | 434 | 532
Min Selected Airflow [m] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Min Permissible Airflow @ ΔT = -12K | 13.6 | 28.8 | 43.6 | 58.1 | 73.3 | 88.9 | 103.3 | 118.5
Min % Turndown to | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Min Permissible % Turndown to | 14% | 29% | 44% | 58% | 73% | 89% | 103% | 118% |  | Pa | Round
Max Static Pressure (Pa) | 107.8 | 25.9 | 11.2 | 5.8 | < 5 | < 5 | < 5 | < 5 | Min Pressure | 5
Max Total Pressure (Pa) | 127 | 28.4 | 12.4 | 7 | < 5 | < 5 | < 5 | < 5 | Converted | 5 | 1
Max Permissible Pressure (Pa) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Sound Power Level (dBA) | 44.9 | 36.9 | 29.2 | 21.2 | 16.9 | < 15 | < 15 | < 15
Sound Pressure Level (NC) | 29.9 | 21.9 | 14.2 | < 10 | < 10 | < 10 | < 10 | < 10
Air Pattern Setting | A | A | A | A | A | A | A | A
Centre Zones with Direction 'A' | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 13.3 | Centre Zones for Air Direction 'A' [K]
Perimeter Zones with Direction 'A' | 15 | 15 | 15 | 15 | 13.3 | 11.6 | 10.1 | 8.8 | Perimeter Zones for Air Direction 'A' [K]
Max Permissible ΔT (heating) E (K) | 20 | 20 | 20 | 13.8 | 9.3 | 6.7 | 5.1 | 4 | Max Permissible ΔT (heating) E (K)
Max Coverage Dist Centre Zone | 19.7 | 15.8 | 14.6 | 14.1 | 13.7 | 13.5 | 13.3 | 13.2
Max C/L Distance (m) Perimeter | 19.7 | 15.8 | 14.6 | 14.1 | 13.7 | 13.5 | 13.3 | 13.2
Min C/L Distance (m) | 8.3 | 5.4 | 4.9 | 4.7 | 4.6 | 4.5 | 4.4 | 4.4
Min Diffuser Height (m) | 2.3 | 2.4 | 2.4 | 2.5 | 2.5 | 2.6 | 2.6 | 2.6
Mean Room Air V | 0.17 | 0.15 | 0.14 | 0.14 | 0.13 | 0.13 | 0.13 | 0.13
Draught Rating | 16.7% | 13.8% | 12.9% | 12.4% | 12.1% | 11.9% | 11.7% | 11.6%
PPD | 8.6% | 7.4% | 7% | 6.9% | 6.7% | 6.7% | 6.6% | 6.6%
PMV | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
PPD Class | B | B | B | B | B | B | B | B
Thermal Element Setting | n.r. | n.r. | n.r. | 30† | 29 | 27 | 25 | 24
Warm-Up Max Boost DT |  |  |  | 14 | 13.3 | 10.7 | 9.1 | 8
Warm-Up Airflow Boost |  |  |  | 1.009 | 1.1967 | 1.2643 | 1.3366 | 1.4134
Warm-Up Pressure Boost |  |  |  | 1.0181 | 1.4321 | 1.5984 | 1.7866 | 1.9977
Diffusers Active During Warm-Up Boost |  |  |  | 99.11% | 83.56% | 79.1% | 74.81% | 70.75%
Nominal Spigot Size / 1200 mm | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | 1200 mm
ADPI actual (centre) | 90% | 95% | 95% | 95% | 95% | 95% | 95% | 95%
ADPI actual (perim) | 90% | 95% | 95% | 95% | 95% | 95% | 95% | 95%
thermal element note |  |  |  | †
Thermal element velocity note |  |  |  | mid
Shading | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
lowpressure | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE
max flow | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE |  | True = Shade
min flow | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
c_select > cmax centre | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | OR | AND
c_select > cmax perimeter | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
cmin>cmax centre | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
cmin>cmax perim | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
C centre | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
C perim | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
selected dist < cmin | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | OR | AND
[9 empty] | FALSE | FALSE
diffuser height | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
Shade | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE
Heating Display
Max Permissible DT
Dimensions
Notes
Charts |  |  |  |  | 2x Line
x-1 | -12 | y1 | 10 |  | x-2 | -6 | y2 | 10
x-2 | -6 | y2 | 10 |  | x1 | #VALUE! | y4 | 2
x0 | 0 | y3 | #VALUE! |  | intercept | #VALUE!
x1 | Max Permissible ΔT (heating) E (K) | y4 | 2
[5 empty] | 1 Slot | 2 Slots | 3 Slots | 4 Slots | 5 Slots | 6 Slots
Width Flangeless Face (Wn) |  |  |  |  | 43.5 | 85.5 | 127.5 | 169.5 | 211.5 | 253.5 | mm
Width Flanged Face (Wf) |  |  |  |  | 72 | 114 | 156 | 198 | 240 | 282 | mm
Width of Diffuser Throat (Wt) |  |  |  |  | 38 | 80 | 122 | 164 | 206 | 248 | mm
Recommended Internal Plenum Height A * |  |  |  |  | D + 76 | [5 empty] | mm
Recommended Internal Plenum Width B * |  |  |  |  | 93.5 | 135.5 | 177.5 | 219.5 | 261.5 | 303.5 | mm
[5 empty] | 1 Slot | 2 Slots | 3 Slots | 4 Slots | 5 Slots | 6 Slots
Width Flangeless Face (Wn) |  |  |  |  | 43.5 | 85.5 | 127.5 | 169.5 | 211.5 | 253.5 | mm
Width Flanged Face (Wf) |  |  |  |  | 72 | 114 | 156 | 198 | 240 | 282 | mm
Width of Diffuser Throat (Wt) |  |  |  |  | 38 | 80 | 122 | 164 | 206 | 248 | mm
Recommended Internal Plenum Height A * |  |  |  |  | D + 76 | [5 empty] | mm
Recommended Internal Plenum Width B * | [5 empty] | 135.5 | 177.5 | 219.5 | 261.5 | 303.5 | mm
Diagram
Textbox1 | 63 | 63
Textbox2 | 35 | 35
Acoustic Notes table
single unit | 1 | 4
0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | m
-3.0103 | 0 | 3.0103 | 4.7712 | 6.0206 | 6.9897 | 7.7815 | 8.451
2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | ft
-3.0103 | -1.2494 | 0 | 0.9691 | 1.7609 | 2.4304 | 3.0103 | 3.5218
0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7
-3 | 0 | 3 | 4.8 | 6 | 7 | 7.8 | 8.5

## data (hidden)
ADPI
95% | 0.2
90% | 0.25
80% | 0.29
70% | 0.33
nslots | 0 | 0
|  | code | type | display | note
Length | 1 | N1200 | Neck | 1200* mm (neck) | 1200 mm neck length
| 2 | F1195 | Face | 1195 mm (face) | 1195 mm face length
| 3 | <length> | neck length | custom^ ≤ 1200 mm (neck) | custom neck length
| 1 | N1200 | Neck | 1200* mm (neck) | 1200 mm neck length
|  | Options | Code | Type | Display | Note
|  | 1 | N1200 | Neck | 1200* mm (neck) | 1200 mm neck length
|  | 2 | F1195 | Face | 1195 mm (face) | 1195 mm face length
|  | 3 | <length> | neck length | custom^ ≤ 1200 mm (neck) | custom neck length
|  | 1 | N4' | Neck | 4 ft.* (neck) | 4 ft. neck length
|  | 2 | F3'11.8 | Face | 3 ft. 11.8 in. (face) | 3 ft. 11.8 in. face length
|  | 3 | <length> | neck length | custom^ ≤ 4 ft (neck) | custom neck length
Supply Return |  | Code | Description | Comment
| 1 | AD | supply | see 'Notes' Row 16 for performance adjustments as a return air inlet | LJC-AD (supply air)
| 2 | RA | return air |  | LJC-RA (return air)
| 3 | RA2 | return air 2 |  | LJC-RA2 (return air boosted)
| 1 | AD | supply | see 'Notes' Row 16 for performance adjustments as a return air inlet | LJC-AD (supply air)
| Supply Air Selected | TRUE
Air Pattern | 2
Colour | RAL9003 | 1 | RAL9005 (jet black)
Barrel | B | 1
Air Direction | 1 | 2 | 3 | 4 | 5 | 6 | 7
1way text | recommended | AB | AC | BC | BD | EE (vertical) | custom
2way text | recommended | A (0 to -15°) | B (0 to -30°) | C (≈ -45°) | D (≈ -60°) | E (vertical) | custom
2way text | recommended | A (0 to -15°) | B (0 to -30°) | C (≈ -45°) | D (≈ -60°) | E (vertical) | custom
1way code |  | AB | AC | BC | BD | EE | <direction>
2way code |  | A | B | C | D | E | <direction>
Result | Air Pattern Setting | A | B | C | D | E | <direction>
Air Direction | Air Pattern Setting | 1
Adjustment Type
Shading | M | T | E
|  | 0 | 0
Slots
|  | Code | Description | Comment | Note type 2
| 0 |  | <adj.type>
| 1 | M.Air Pattern Setting | manual | manual adjustment only
| 2 | TThermal Element Setting | thermal actuator | thermal actuator set to Th°Cthermal element note
| 3 | E1 | electric actuator | 24V electric actuator 2-10V | 24V electric actuator 2-10V (see recommended control curve below)
| 4 | E2 | electric actuator | 24V electric actuator 3-pt | 24V electric actuator 3pt
Selection | 1 | M.Air Pattern Setting | manual | manual adjustment only | 0
Side Profile |  | Code | Description
| 1 | SF | with side flanges
| 2 | SN | flangeless side profile
Selection | 1 | SF | with side flanges
Diffuser Ends
|  | Code | Description
| 1 | DE2 | with two end flanges
| 2 | DE1 | with one end flange + one pair of joining strips
| 3 | DEJ | include one pair of joining strips
| 4 | DE0 | without end flanges
Selection | 1 | DE2 | with two end flanges
Fixing |  | Code | Description
| 1 | F0 | fixing by others; without accessories
| 2 | EX | expansion bracket fixing
| 3 | MFP | mounting frame for plasterboard
Selection | 1 | F0 | fixing by others; without accessories
connection box
| 1 | K0 | no connection box
| 2 | K | uninsulated connection box
| 3 | KI | internally insulated connection box
Selection | 1 | K0 | no connection box
0
| 1 | t | clipped to diffuser throat
| 2 | n | screwed to diffuser throat
Selection | 0
0
Selection |  | K0 | no connection box
Naming
Supply | Supply/Return | nominal length | nslots | airpattern num | adj type | profile type | diffuserends | fixing | profile colour | barrelcolour | Box
SMARTEMP LJC- | AD- | N1200- | 0- | 2W- | M.Air Pattern Setting- | SF- | DE2- | F0- | RAL9003- | B- | K0
Return | Supply/Return | nominal length | nslots | airpattern num | adj type | profile type | diffuserends | fixing | profile colour | barrelcolour | Box
SMARTEMP LJC- | AD- | N1200- | 0- |  |  | SF- | DE2- | F0- | RAL9003- | B- | K0
Supply | Please select length and number of slots | SMARTEMP LJC-AD
Return | Please select length and number of slots | SMARTEMP LJC-RA
product code | Please select length and number of slots | SMARTEMP LJC-AD
Bespoke dimensions
Summary
Length
Slots | please select number of
Size | 1200 mm neck length × please select number of slots
Air pattern | 2-way blow
Location | Closed Ceiling
|  |  | Units | Format
0 | Slots | Slots
1 | Selected Airflow [L/s/m] | Selected Airflow [L/s] | L/s/m | Selected Airflow [L/s] L/s/m
2 | Airflow @ Max Static Pressure[L/s/m] | Airflow @ Max Static Pressure[L/s] | L/s/m | Airflow @ Max Static Pressure[L/s] L/s/m
3 | Min Selected Airflow [L/s/m] | Min Selected Airflow [m] | L/s/m | Min Selected Airflow [m] L/s/m
4 | Min Permissible Airflow @ -12 K | Min Permissible Airflow @ ΔT = -12K
5 | Min % Turndown to | Min % Turndown to |  | #VALUE!
6 | Min Permissible % Turndown to | Min Permissible % Turndown to
7 | Max Static Pressure (Pa) | Max Static Pressure (Pa) | Pa | Max Static Pressure (Pa) Pa
8 | Max Total Pressure (Pa) | Max Total Pressure (Pa) | Pa | Max Total Pressure (Pa) Pa
9 | Max Permissible Pressure (Pa) | Max Permissible Pressure (Pa) | Pa | Max Permissible Pressure (Pa) Pa
10 | Sound Power Level (dBA) | Sound Power Level (dBA) | db(A)/m | Sound Power Level (dBA) db(A)/m
11 | Sound Pressure Level (NC) | Sound Pressure Level (NC) | NC/m | Sound Pressure Level (NC) NC/m
12 | Air Pattern Setting | Air Pattern Setting
13 | Centre Zones with Direction 'C' | Centre Zones with Direction 'A' | K | +Centre Zones with Direction 'A' K
14 | Perimeter Zones with Direction 'C' | Perimeter Zones with Direction 'A' | K | +Perimeter Zones with Direction 'A' K
15 | Max Permissible ΔT (heating) E (K) | Max Permissible ΔT (heating) E (K) | K | +Max Permissible ΔT (heating) E (K) K
16 | Max Coverage Dist Centre Zone | Max Coverage Dist Centre Zone | m | Max Coverage Dist Centre Zone m
17 | Max C/L Distance (m) Perimeter | Max C/L Distance (m) Perimeter | m | Max C/L Distance (m) Perimeter m
18 | Min C/L Distance (m) | Min C/L Distance (m) | m | Min C/L Distance (m) m
19 | Min Diffuser Height (m) | Min Diffuser Height (m) | m | Min Diffuser Height (m) m
20 | Mean Room Air V | Mean Room Air V | m/s | Mean Room Air V m/s
21 | Draught Rating | Draught Rating
22 | PPD | PPD
23 | PMV | PMV
24 | PPD Class | PPD Class
25 | Thermal Element Setting | Thermal Element Setting |  | Th
26 | Warm-Up Max Boost DT | Warm-Up Max Boost DT | K
27 | Warm-Up Airflow Boost | Warm-Up Airflow Boost
28 | Warm-Up Pressure Boost | Warm-Up Pressure Boost
29 | Diffusers Active During Warm-Up Boost | Diffusers Active During Warm-Up Boost
30 | Nominal Spigot Size | Nominal Spigot Size / 1200 mm
31 | ADPI actual (centre) | ADPI actual (centre) | #VALUE!
32 | ADPI actual (perim) | ADPI actual (perim) | #VALUE!
33 | t element note | thermal element note
34 | t element category | Thermal element velocity note | #N/A |  | high | moderately elevated air velocities in heating
[5 empty] | mid | slightly elevated air velocities in heating
|  | units | format
dt | -12 | K | -12 K
room temp | 23 | °C | 23 °C
dist type selection | 1
height | 2.7 | m | 2.7 m
Units | L/s/m | 1
Summary | Summary (valid as supply air only)
Summary | Text
Airflow | Selected Airflow [L/s] L/s/m @ Max Total Pressure (Pa) Pa total (Max Static Pressure (Pa) Pa static)
Min airflow | #VALUE! | #VALUE!
Heating non vertical | +Centre Zones with Direction 'A' K for centre zones; +Perimeter Zones with Direction 'A' K for perimeter zones (pattern 'Air Pattern Setting')
Heating vertical | +Max Permissible ΔT (heating) E (K) K for vertical discharge (pattern 'E')
Max Heating | +Centre Zones with Direction 'A' K for centre zones; +Perimeter Zones with Direction 'A' K for perimeter zones (pattern 'Air Pattern Setting') | +Centre Zones with Direction 'A' K for centre zones; +Perimeter Zones with Direction 'A' K for perimeter zones (pattern 'Air Pattern Setting')
airdischarge (manual) | discharge direction manually set to 'Air Pattern Setting'
airdischarge (actuated) | directional adjustment with manual adjustment only
Acoustic
SWL | Sound Power Level (dBA) db(A)/m
SPL | Sound Pressure Level (NC) NC/m
Recommended Connection Box Spigot Diameter per 1200 mm length | Nominal Spigot Size / 1200 mm mm | 1200 mm length
Comfort Performance
ADPI | #VALUE! | #VALUE!
Mean Room Air Velocity | Mean Room Air V m/s | Mean Room Air V m/s
Mean Draught Rating | #VALUE! | #VALUE!
Mean PPD | #VALUE! | #VALUE!
Satisfies PPD (ISO7730) | Category PPD Class | Category PPD Class
Mean PMV * | -PMV < PMV < +PMV | -PMV < PMV < +PMV
Diagram
Selected ADPI | Recommended distances for ≥ 90% ADPI (Selected)
Cmin | Min C/L Distance (m)
Cmax Cenre | Max Coverage Dist Centre Zone m
Cmax Perim | Max C/L Distance (m) Perimeter m
Text | C Max (centre/perimeter) = Max Coverage Dist Centre Zone m / Max C/L Distance (m) Perimeter m
C Min = Min C/L Distance (m) m
Nominal
C Select | 9.9 m | 9.9 | m
| 5.03 L/s/m² | 5.03 | L/s/m²
Nominal C = 9.9 m
box1 | C Max (centre/perimeter) = Max Coverage Dist Centre Zone m / Max C/L Distance (m) Perimeter m | C Max (centre/perimeter) = Max Coverage Dist Centre Zone m / Max C/L Distance (m) Perimeter m | 1 | Specific Airflow Rate = 5.03 L/s/m² @ Average C of 9.9 m
box2 | C Min = Min C/L Distance (m) m | C Min = Min C/L Distance (m) m | 2 | Specific Airflow Rate = 5.03 L/s/m² @ Selected C of 9.9 m
box3 | Nominal C = 9.9 m | Nominal C = 9.9 m | 3 | Specific Airflow Rate = 5.03 L/s/m²
room box | Specific Airflow Rate = 5.03 L/s/m² @ Average C of 9.9 m | Specific Airflow Rate = 5.03 L/s/m² @ Average C of 9.9 m
Height | Selected Diffuser Height = 2.7 m | Selected Diffuser Height = 2.7 m
| Min Recommended Diffuser Height = Min Diffuser Height (m) m | Min Recommended Diffuser Height = Min Diffuser Height (m) m
Return Air Display Note
1. Use setting 'C' for R/A.
2. R/A diffuser pressure loss is up to 25% greater than supply air static pressure.
3. R/A diffuser sound power level is up to 3 db(A) greater than the supply air sound power level.
1. R/A boosted: If three out of every four barrels are removed, then R/A airflow may be doubled without exceeding the above stated pressure loss and sound power levels.
1
2
3
Adjustment
M | Manual adjustment
T | Thermal actuator set to Th°Cthermal element note
E | 0
M2 | Manual adjustment only for return air
M | Manual adjustment
Thermal Element Note display
Front Page Selection Section
Default Inputs | SI | SI2 | Imperial | Named Range
Radio Button Ref. | 1 | 2 | 3
Maximum Airflow Rate | 100 | 360 | 220 | 100
VAV (turndown to) | 100 | 100 | 100 | 100
Maximum Permissible Static Pressure | 30 | 30 | 0.121 | 30
ΔT (cooling) | -12 | -12 | -22 | -12
Diffuser Height | 2.7 | 2.7 | 9 | 2.7
Active Length Ratio (see diagram) | 0.5 | 0.5 | 0.5 | 0.5
ADPI ≥ | 90% | 90% | 90% | 0.9
Manual Diffuser Coverage | 7 | 7 | 23 | 7
Specific Airflow Rate | 5 | 18 | 1 | 5
Room Temperature (cooling) | 23 | 23 | 73 | 23
Room Temperature (heating) | 21 | 21 | 70 | 21
Room Temp. @ heating startup | 16 | 16 | 61 | 16
% Low Level Return (heating) | 0 | 0 | 0 | 0
Note Values
Maximum Permissible Static Pressure | 30 | 30 | 0.121 | 30
DT high | -16 | -16 | -29 | -16
height heat and cool | 2 | 2 | 7 | 2
| 10 | 10 | 33 | 10
height cool | 15 | 15 | 49 | 15
avg distance | 9.9 | 9.9 | 32.5 | 9.9
max spec flowrate | 30 | 108 | 5.91 | 30
room temp cooling draught rating | 20 | 20 | 68 | 20
| 26 | 26 | 79 | 26
auto room temp heating | 21 | 21 | 69.8 | 21
night setback note | 16 | 16 | 61 | 16
selected/nominal/avg distance | 9.9 | 9.9 | 32.5 | 9.9
Notes |  | Values
Maximum Permissible Static Pressure | default 30 Pa
DT | 0K to -16K (default -12K) | 0K | -16K | -12K
Height Heat & Cool | 2 m to 10 m (heating and cooling) | 2 m | 10 m
Height Cooling | 2 m to 15 m (cooling only) | 2 m | 15 m
diffuser coverage | nominal distance = 9.9 m | 9.9 m
Manual coverage | average specific flow rate: 5.03 L/s/m² | 5.03 L/s/m²
spec flow rate | ≤ 30 L/s/m²
spec flow coverage | average diffuser coverage: 10 m | 10 m
room temp cooling | 20 °C to 26 °C (for draught rating) | 20 °C | 26 °C
auto room temp heating | auto room temp. (heating) = 21 °C | 21 °C
night setback note | night setback temperature default (16 °C) | 16 °C
Units
heat gradient (horizontal) | Rows 55:56: Typical max vertical temperature gradient 2 to 3°C/m | 2 | 3 | °C/m
heat gradient (vertical) | Row 57: Typical vertical temperature gradient ≤ 1°C/m | 1 |  | °C/m
Vertical discharge: manual setting 'E' or with thermal/electric actuator.
Thermal and electric actuator available for 2 slots or more only.
Display Note | Rows 55:56: Typical max vertical temperature gradient 2 to 3°C/m Row 57: Typical vertical temperature gradient ≤ 1°C/m Vertical discharge: manual setting 'E' or with thermal/electric actuator. Thermal and electric actuator available for 2 slots or more only.
Text
nominal | Nominal
Display | FALSE
C selected note warning |  | Rows 58-59: Nominal coverage distance > Cmax.
Cmin>Cmax Note |  | Rows 58-60: Threat of draught when Cmin > Cmax Consider: increasing 'Active Length Ratio'; increasing 'Turndown To'; decreasing 'ADPI'
C selected note warning |  | Row 60: Nominal coverage distance < Cmin.
diffuser height |  | Row 61: Selected height (cell E17) < Min recommended height
Note
Comfort note | Comfort criteria valid for diffuser spacing of 9.9 m & room temperature of 23°C (see cells L18:L21 & L23)
Description | LJC-AD (supply air)
| 1200 mm neck length; (number of slots not selected) | 1200 mm neck length | (number of slots not selected)
2-way blow
discharge direction manually set to 'Air Pattern Setting'
| profile powder coated to RAL9003 with black barrels | RAL9003 | black
with side flanges
with two end flanges
fixing by others; without accessories
no connection box
Product Select Description | • LJC-AD (supply air) | • profile powder coated to RAL9003 with black barrels
| • 1200 mm neck length; (number of slots not selected) | • with side flanges
| • 2-way blow | • with two end flanges
| • discharge direction manually set to 'Air Pattern Setting' | • fixing by others; without accessories
• no connection box
| • LJC-AD (supply air) • 1200 mm neck length; (number of slots not selected) • 2-way blow • discharge direction manually set to 'Air Pattern Setting' | • profile powder coated to RAL9003 with black barrels • with side flanges • with two end flanges • fixing by others; without accessories • no connection box

## Selection Summary & Print
| LJC-AD Performance Calculator Summary |  |  |  | LJC-AD Performance Calculator Summary
Project | <Project Name> |  |  | Direction Adjustment | Manual adjustment
Diffuser Location | <Name>
Consultant | <Name>
|  |  |  | Description | LJC-AD (supply air)
Product | SMARTEMP LJC-AD |  |  |  | 1200 mm neck length; (number of slots not selected)
| Linear Multi-Jet Adjustable Diffuser |  |  |  | 2-way blow
Size | 1200 mm neck length × please select number of slots |  |  |  | profile powder coated to RAL9003 with black barrels
Discharge Pattern | 2-way blow |  |  |  | with side flanges
Diffuser Location | Closed Ceiling |  |  |  | with two end flanges
fixing by others; without accessories
Summary |  |  |  |  | no connection box
Selected Airflow | Selected Airflow [L/s] L/s/m @ Max Total Pressure (Pa) Pa total (Max Static Pressure (Pa) Pa static)
Min Selected Airflow (Supply) | #VALUE!
Max Recommended Heating ΔT | +Centre Zones with Direction 'A' K for centre zones; +Perimeter Zones with Direction 'A' K for perimeter zones (pattern 'Air Pattern Setting')
Acoustic Performance |  |  |  | Order Code (select to copy) | Please select length and number of slots
Sound Power Level | Sound Power Level (dBA) db(A)/m
Sound Pressure Level ^ | Sound Pressure Level (NC) NC/m | ^ based on 10dB room absorption |  | Recommended Control Curve (for electric actuator 2-10V)
Recommended Connection Box Spigot Diameter per 1200 mm length | Nominal Spigot Size / 1200 mm mm
Comfort Performance
ADPI | #VALUE!
Mean Room Air Velocity | Mean Room Air V m/s
Mean Draught Rating | #VALUE!
Mean PPD | #VALUE!
Satisfies PPD (ISO7730) | Category PPD Class
Mean PMV * | -PMV < PMV < +PMV
* ISO7730; ASHRAE Std 55
v 3.3 [02/2025]
v 3.3 [02/2025]
C Max (centre/perimeter) = Max Coverage Dist Centre Zone m / Max C/L Distance (m) Perimeter m
Nominal C = 9.9 m
C Min = Min C/L Distance (m) m
Min Recommended Diffuser Height = Min Diffuser Height (m) m
Selected Diffuser Height = 2.7 m
Recommended distances for ≥ 90% ADPI (Selected)
Specific Airflow Rate = 5.03 L/s/m² @ Average C of 9.9 m

## Notes
SMARTEMP PRODUCT SELECTION CALCULATOR
Linear Multi-Jet Ceiling Diffuser [LJC-AD] Notes
NOTES
ΔT -ve denotes cooling |  |  | ΔT +ve denotes heating
Pressure is inclusive of side-entry connection box pressure loss.
Centreline distance is the spacing between two 2-way blow diffuser rows. Halve this value for throw to walls or maximum throw of a 1-way diffuser. Refer to Diffuser Location notes below.
Select desired comfort level (ADPI setting) to determine minimum and maximum spacing or throw (centreline distances) and minimum discharge height.
NOISE AND ACOUSTIC
Sound Pressure Level [NC] is an estimate for a single diffuser only located at 2.7 to 3.0 m height in a 70 m3 space (typical office) with 10 dB(A) room absorption that is uniformly distributed, measured 2.1 m from the diffuser. Sound Pressure Level is provided as a guide only for a standard, carpeted single office with acoustic ceiling. An acoustical engineer should be consulted for detailed calculations, especially for applications with more than one diffuser or where hard surfaces are involved.
Adjustments to Noise Levels (Row 52 & 53)
Length |  | [m] | 0.5 | 1 | 2 | 3 | 4 | 5 | 6
SWL adjustment |  | [db(A)] | -3 | 0 | 3 | 4.8 | 6 | 7 | 7.8
SPL adjustment |  | [NC]
DIFFUSER AS RETURN AIR (R/A) INLET
1. Use setting 'C' for R/A.
2. R/A diffuser pressure loss is up to 25% greater than supply air static pressure.
3. R/A diffuser sound power level is up to 3 db(A) greater than the supply air sound power level.
4. R/A boosted: If three out of every four barrels are removed, then R/A airflow may be doubled without exceeding the above stated pressure loss and sound power levels.
ACTIVE LENGTH RATIO
Active Length Ratio = LA / L |  |  | where: | LA = ∑ LA,i | and
LA ≥ 0.1 ∙ L
Refer to Figure (right) for description of lengths 'L' and 'LA'
|  |  |  | e.g. Active Length Ratio | = (1.2+1.2)/4.8
= 0.5
LAYOUT/COVERAGE DISTANCE
|  | For 2-Way Discharge | [6 empty] | For 1-Way Discharge
PRE-OCCUPANCY WARM-UP BOOST
For warm-up from a low night setback temperature (cell L27), especially where high infiltration heat loss occurs (e.g. lobbies), consider introducing a Pre-Occupancy Warm-Up Boost mode that increases diffuser airflow by the Airflow Boost Factor (row 61) and pressure by the Pressure Boost Factor (row 74) during pre-occupancy warm-up only. This is typically achieved by either:
1. | Speeding up the supply fan to increase total airflow by the Airflow Boost Factor (row 74); or
2. | By not increasing total airflow, but instead only supplying air to the percentage of Diffusers Active During Warm-Up Boost (row 76), typically achieved by having motorised dampers (by others) shut off airflow to the remaining diffusers (typically to a duct run of diffusers). Round up/down the percentage to avoid fractions of diffusers to which airflow is to be shut-off. Minimise motorised dampers by grouping diffusers to be shut-off onto common ducts. Refer to example below.
Pre-Occupancy Warm-Up is to be deactivated when room temperature setpoint is achieved, and is to remain deactivated until the next warm-up cycle is initiated.
Example of Option 2, above:
Selected Airflow |  |  | 110 L/s @ 13.6 Pa static
Room Temperature Setpoint |  |  | 22°C
Night Setback Temperature |  |  | 16°C
Results: | [5 empty] | Explanation:
Row 59 | Thermal Element Setting |  |  |  | 27°C | - Supply air to be greater than or equal to 27 °C, otherwise the guide-ring will retract and prevent heat project to the floor.
Row 60 | Warm-Up Max Boost ΔT |  |  |  | 11.3 K
Row 61 | Warm-Up Airflow Boost Factor |  |  |  | 1.43 | - Boosted Airflow per diffuser: 1.43 × 110 L/s = 157 L/s
Row 62 | Warm-Up Pressure Boost Factor |  |  |  | 2.05 | - Pressure required to achieve Boosted Airflow: 2.05 × 13.6 = 27.9 Pa
Row 63 | Diffusers Active During Warm-Up Boost |  |  |  | 70% | - Boost airflow by supplying the fixed total airflow only to the percentage of Diffusers Active During Warm-Up (70%), achieved by shutting off airflow, via motorised dampers, to the remaining diffusers (i.e. 30%).
AIR DIRECTION SETTINGS
A | 0⁰ to -15⁰ discharge to the horizontal
B | 0⁰ to -30⁰ discharge to the horizontal
C | ≈ -45⁰ discharge to the horizontal
D | ≈ -60⁰ discharge to the horizontal
E | vertical discharge
DEFAULT VALUES
The default expression is entered as a formula.
Field |  |  |  | Default Value (SI) (L/s/m) |  | Default Value (SI) (m3/h/m) |  | Default Value (I-P) (ft³/min/ft) |  | Default Expression | e.g.
Maximum Airflow Rate |  |  |  | 100 |  | 360 |  | 220 |  | _defaultAirflow | Maximum Airflow Rate | =_defaultAirflow
VAV (turndown to) |  |  |  | 100 |  | 100 |  | 100 |  | _defaultVAV
Maximum Permissible Static Pressure |  |  |  | 30 |  | 30 |  | 0.121 |  | _defaultPressure
ΔT (cooling) |  |  |  | -12 |  | -12 |  | -22 |  | _defaultDT
Diffuser Height |  |  |  | 3.2 |  | 3.2 |  | 10 |  | _defaultHeight
Active Length Ratio (see diagram) |  |  |  | 0.5 |  | 0.5 |  | 0.5 |  | _defaultRatio
Air Pattern |  |  |  | 2-Way |  | 2-Way |  | 2-Way
ADPI |  |  |  | 90% |  | 90% |  | 90%
Diffuser Location |  |  |  | Closed Ceiling |  | Closed Ceiling |  | Closed Ceiling
Diffuser Coverage |  |  |  | - |  | - |  | -
Manual Diffuser Coverage |  |  |  | 7 |  | 7 |  | 23 |  | _defaultCoverage
Specific Airflow Rate |  |  |  | 5 |  | 18 |  | 1 |  | _defaultSpecFlow
Room Temperature (cooling) |  |  |  | 23 |  | 23 |  | 73 |  | _defaultTempCool
Room Tempreture (heating) |  |  |  | 21 |  | 21 |  | 70 |  | _defaultTempHeat
Room Temp. @ heating startup |  |  |  | 16 |  | 16 |  | 61 |  | _defaultSetback
% Low Level Return (heating) |  |  |  | 0 |  | 0 |  | 0 |  | _defaultLowLevel

## Diffuser Layout (not used) (hidden)
SMARTEMP PRODUCT SELECTION CALCULATOR
Linear Multistream Ceiling Diffuser [LMC-AD] Notes
Notes
Total pressure is inclusive of side-entry connection box pressure loss.
Centreline distance is the spacing between two 2-way blow diffuser rows. Halve this value for throw to walls or maximum throw of a 1-way diffuser. Refer to Diffuser Location notes below.
Select desired comfort level (ADPI setting) to determine minimum and maximum spacing or throw (centreline distances) and minimum discharge height.
Sound pressure level [NC] is valid in a standard commercial office with a 2.7 m to 3 m ceiling.
Inputs
Active Length Ratio = LA / L |  |  | where: | LA = ∑ LA,i | and | e.g. |  | Active Length Ratio | = (1.2+1.2)/4.8
|  |  |  | LA ≥ 0.1 ∙ L |  |  |  |  | = 0.5
Refer to Fig. 1, Fig. 2 for description of lengths 'L' and 'LA'
Diffuser Distance
| For 2-Way Blow |  | 100 | L/s/m |  |  | For 1-Way Blow (not selected) |  |  | 100 | L/s/m
| C | #REF!
| C/2 | #REF!
C/4
C/8
ALL DIMENSIONS IN m
Air Direction Settings
A | 0⁰ to -15⁰ discharge to the horizontal
B | 0⁰ to -30⁰ discharge to the horizontal
C | ≈ -45⁰ discharge to the horizontal
D | ≈ -60⁰ discharge to the horizontal
E | vertical discharge
Sound
Sound Pressure Level (NC/m) based on 10 dB room absorption
Air Direction D
#REF!
#REF!
Figure 1
Figure 2
Air Direction A
Air Direction B
Air Direction C
1.2 m
1.2 m
4.8 m
0 to -15°
0 to -30°
≈ -45°
≈ -60°

## Dimensions & Connection Box
SMARTEMP PRODUCT SELECTION CALCULATOR
Linear Multi-Jet Ceiling Diffuser [LJC-AD] Dimensions
Dimensions
DIMENSIONS IN mm
|  |  |  | 1 Slot | 2 Slots | 3 Slots | 4 Slots | 5 Slots | 6 Slots
|  | Width Flangeless Face (Wn) |  | 43.5 | 85.5 | 127.5 | 169.5 | 211.5 | 253.5 | mm
|  | Width Flanged Face (Wf) |  | 72 | 114 | 156 | 198 | 240 | 282 | mm
|  | Width of Diffuser Throat (Wt) |  | 38 | 80 | 122 | 164 | 206 | 248 | mm
|  | Recommended Internal Plenum Height A * |  | D + 76 | [5 empty] | mm
|  | Recommended Internal Plenum Width B * |  | 63 | 135.5 | 177.5 | 219.5 | 261.5 | 303.5 | mm
|  | Recommended Spigot Dimension D * per 1 m length | [8 empty] | mm
|  | Recommended Spigot Dimension D * per 1.2 m length | [8 empty] | mm
|  | Recommended Spigot Dimension D * per 1.5 m length | [8 empty] | mm
|  |  | * | Plenum box dimensions are for internal dimensions (excludes insulation and acoustic lining)
|  |  | * | Check exact dimensions with local supplier
63
35
63
63
63
63
63

## charts (hidden)
Electric and Thermal Actuators available for 2+ slots only
Control Curve N/A for return air inlet
Recommended Actuator Control for 0 slot at Max Airflow at 2.7 m | 2.7 m
Recommended Actuator Control for 0 slot at Max Airflow at 2.7 m
cooling
heating